## atc138_ds_mapping_combined
[12 empty] | Safety | [5 empty] | Access | Function |  |  | Interior Impact |  | Repair Schedule
1 | fragility_id_regex | component_type | str_or_ns | major | minor | spirit_of_damage | fragilities | description | repair_measures | ds_index | sub_ds_index | safety_class | affects_envelope_safety | exterior_falling_hazard | interior_falling_hazard | global_hazardous_material | local_hazardous_material | affects_access | damages_envelope_seal | obstructs_interior_space | impairs_system_operation | fraction_area_affected | area_affected_unit | crew_size | has_tmp_fix | tmp_fix_time | requires_shoring | permit_type | redesign
0 | B1029\.1\w+ | Flexible Wood Diaphram for Tilt-Up Roof Systems | Structural | Roof | Flexible Diaphragm | Tearing of roofing materials and flashing at supports. Some nail slippage and withdrawl at the diaphragm center and corners. | 1/9: B1029.101 - Flexible wood diaphragm, pre 1976, plan aspect ratio 1:1. 2/9: B1029.102 - Flexible wood diaphragm, pre 1976, plan aspect ratio 2:1. 3/9: B1029.103 - Flexible wood diaphragm, pre 1976, plan aspect ratio 1:2. 4/9: B1029.111 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 1:1. 5/9: B1029.112 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 2:1. 6/9: B1029.113 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 1:2. 7/9: B1029.121 - Flexible wood diaphragm, post 1996, plan aspect ratio 1:1. 8/9: B1029.122 - Flexible wood diaphragm, post 1996, plan aspect ratio 2:1. 9/9: B1029.123 - Flexible wood diaphragm, post 1996, plan aspect ratio 1:2. | (all): Tearing of roofing materials and flashing at supports. Some nail slippage and withdrawl at the diaphragm center and corners. | (all): Remove the existing flashing and 4-feet of roofing material along the wall. Remove damaged nails and install new nails where no splitting of the frame has occurred (25% of nails over the 4 foot width). Remove and replace plywood and framing including ledgers at split framing or damaged plywood (25% of the 4 foot width). | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1029\.1\w+ | Flexible Wood Diaphram for Tilt-Up Roof Systems | Structural | Roof | Flexible Diaphragm | Nails pull out, framing splitting and plywood tearing extends into the diaphragm. | 1/9: B1029.101 - Flexible wood diaphragm, pre 1976, plan aspect ratio 1:1. 2/9: B1029.102 - Flexible wood diaphragm, pre 1976, plan aspect ratio 2:1. 3/9: B1029.103 - Flexible wood diaphragm, pre 1976, plan aspect ratio 1:2. 4/9: B1029.111 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 1:1. 5/9: B1029.112 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 2:1. 6/9: B1029.113 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 1:2. 7/9: B1029.121 - Flexible wood diaphragm, post 1996, plan aspect ratio 1:1. 8/9: B1029.122 - Flexible wood diaphragm, post 1996, plan aspect ratio 2:1. 9/9: B1029.123 - Flexible wood diaphragm, post 1996, plan aspect ratio 1:2. | (all): Nails pull out, framing splitting and plywood tearing extends into the diaphragm. | (all): Extend DS1 repairs to an 8-foot width, remove damaged nails and install new nails where no splitting of framing occurs (25% of nails over 8 foot width of diaphragm along wall). Remove and replace plywood and framing including ledgers at split framing or damaged plywood (25% of 8 foot width of diaphragm along wall). | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | building | 6 | 0 | 0 | 0 | full | 1
0 | B1029\.1\w+ | Flexible Wood Diaphram for Tilt-Up Roof Systems | Structural | Roof | Flexible Diaphragm | In addition to damage described for DS1 and DS2, plywood panels pull free of sub-framing and framing splits over approximately 25% of the diaphragm span at each diaphragm support. | 1/9: B1029.101 - Flexible wood diaphragm, pre 1976, plan aspect ratio 1:1. 2/9: B1029.102 - Flexible wood diaphragm, pre 1976, plan aspect ratio 2:1. 3/9: B1029.103 - Flexible wood diaphragm, pre 1976, plan aspect ratio 1:2. 4/9: B1029.111 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 1:1. 5/9: B1029.112 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 2:1. 6/9: B1029.113 - Flexible wood diaphragm, 1976 through 1996, plan aspect ratio 1:2. 7/9: B1029.121 - Flexible wood diaphragm, post 1996, plan aspect ratio 1:1. 8/9: B1029.122 - Flexible wood diaphragm, post 1996, plan aspect ratio 2:1. 9/9: B1029.123 - Flexible wood diaphragm, post 1996, plan aspect ratio 1:2. | (all): In addition to damage described for DS1 and DS2, plywood panels pull free of sub-framing and framing splits over approximately 25% of the diaphragm span at each diaphragm support. | (all): Remove and replace roofing, flashing, plywood, framing (girder not replaced) over 25% of diaphragm span and full depth of wall at each diaphragm support. | 3 | NA | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.25 | building | 6 | 0 | 0 | 0 | full | 1
1 | B1029\.3\w+ | Flexible Steel Diaphram for Tilt-Up Roof Systems | Structural | Roof | Flexible Diaphragm | Minor deformations in roof diaphragm connections or hairline cracks in many welded roof connections. Isolated weld or bolt connection failure possible at diaphragm ends. | 1/9: B1029.301 - Flexible steel diaphragm, pre 1976, plan aspect ratio 1:1. 2/9: B1029.302 - Flexible steel diaphragm, pre 1976, plan aspect ratio 2:1. 3/9: B1029.303 - Flexible steel diaphragm, pre 1976, plan aspect ratio 1:2. 4/9: B1029.311 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 1:1. 5/9: B1029.312 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 2:1. 6/9: B1029.313 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 1:2. 7/9: B1029.321 - Flexible steel diaphragm, post 1996, plan aspect ratio 1:1. 8/9: B1029.322 - Flexible steel diaphragm, post 1996, plan aspect ratio 2:1. 9/9: B1029.323 - Flexible steel diaphragm, post 1996, plan aspect ratio 1:2. | (all): Minor deformations in roof diaphragm connections or hairline cracks in many welded roof connections. Isolated weld or bolt connection failure possible at diaphragm ends. | (all): Repair damage to welds and fastener connections. Remove flashing near wall ends to inspect and repair failed connections (approximately 4ft from wall ends). | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1029\.3\w+ | Flexible Steel Diaphram for Tilt-Up Roof Systems | Structural | Roof | Flexible Diaphragm | A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes mainly toward the end roof regions. | 1/9: B1029.301 - Flexible steel diaphragm, pre 1976, plan aspect ratio 1:1. 2/9: B1029.302 - Flexible steel diaphragm, pre 1976, plan aspect ratio 2:1. 3/9: B1029.303 - Flexible steel diaphragm, pre 1976, plan aspect ratio 1:2. 4/9: B1029.311 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 1:1. 5/9: B1029.312 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 2:1. 6/9: B1029.313 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 1:2. 7/9: B1029.321 - Flexible steel diaphragm, post 1996, plan aspect ratio 1:1. 8/9: B1029.322 - Flexible steel diaphragm, post 1996, plan aspect ratio 2:1. 9/9: B1029.323 - Flexible steel diaphragm, post 1996, plan aspect ratio 1:2. | (all): A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes mainly toward the end roof regions. | (all): Extend DS1 repairs to an 8-foot width, repair all damaged welds and bolted connections. Tearing in metal roofing may require localized panel replacement. | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | building | 6 | 0 | 0 | 0 | full | 1
1 | B1029\.3\w+ | Flexible Steel Diaphram for Tilt-Up Roof Systems | Structural | Roof | Flexible Diaphragm | In addition to damage described for DS1 and DS2, some connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections and failed connections. Partial collapse of portions of the roof structure due to failed end connections. | 1/9: B1029.301 - Flexible steel diaphragm, pre 1976, plan aspect ratio 1:1. 2/9: B1029.302 - Flexible steel diaphragm, pre 1976, plan aspect ratio 2:1. 3/9: B1029.303 - Flexible steel diaphragm, pre 1976, plan aspect ratio 1:2. 4/9: B1029.311 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 1:1. 5/9: B1029.312 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 2:1. 6/9: B1029.313 - Flexible steel diaphragm, 1976 through 1996, plan aspect ratio 1:2. 7/9: B1029.321 - Flexible steel diaphragm, post 1996, plan aspect ratio 1:1. 8/9: B1029.322 - Flexible steel diaphragm, post 1996, plan aspect ratio 2:1. 9/9: B1029.323 - Flexible steel diaphragm, post 1996, plan aspect ratio 1:2. | (all): In addition to damage described for DS1 and DS2, some connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections and failed connections. Partial collapse of portions of the roof structure due to failed end connections. | (all): Remove and replace roofing, flashing, framing (girder not replaced) over 25% of diaphragm span and full depth of wall at each diaphragm support. New connections as needed. | 3 | NA | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.25 | building | 6 | 0 | 0 | 0 | full | 1
0 | B1029\.2\w+ | Out-of-plane wall to diaphragm connection for Tilt-Up Roof Systems | Structural | Roof | OOP Conn | Connections fail at one to several bays near the in-plane walls causing the bay nearest the out-of-plane wall to collapse into the building. | 1/9: B1029.201a - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 24 ft. 2/9: B1029.201b - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 27 ft. 3/9: B1029.201c - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 30 ft. 4/9: B1029.202a - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 24 ft. 5/9: B1029.202b - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 27 ft. 6/9: B1029.202c - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 30 ft. 7/9: B1029.203a - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 24 ft. 8/9: B1029.203b - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 27 ft. 9/9: B1029.203c - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 30 ft. | (all): Connections fail at one to several bays near the in-plane walls causing the bay nearest the out-of-plane wall to collapse into the building. | (all): Demo the fallen diaphragm as well was the surrounding diaphragm damaged. Replace the damaged diaphragm, oop wall connections. | 1 | NA | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.25 | building | 6 | 0 | 0 | 0 | full | 1
0 | B1029\.2\w+ | Out-of-plane wall to diaphragm connection for Tilt-Up Roof Systems | Structural | Roof | OOP Conn | Connections fail along an entire wall line precipitating collapse of the wall outward and the diaphragm to the floor of the building. | 1/9: B1029.201a - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 24 ft. 2/9: B1029.201b - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 27 ft. 3/9: B1029.201c - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 30 ft. 4/9: B1029.202a - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 24 ft. 5/9: B1029.202b - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 27 ft. 6/9: B1029.202c - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 30 ft. 7/9: B1029.203a - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 24 ft. 8/9: B1029.203b - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 27 ft. 9/9: B1029.203c - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 30 ft. | (all): Connections fail along an entire wall line precipitating collapse of the wall outward and the diaphragm to the floor of the building. | (all): Demo the fallen wall and diaphragm as well as surrounding damaged components. | 2 | NA | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.5 | building | 6 | 0 | 0 | 0 | full | 1
0 | B1029\.2\w+ | Out-of-plane wall to diaphragm connection for Tilt-Up Roof Systems | Structural | Roof | OOP Conn | Connections fail at one to several bays near the in-plane walls causing the bay nearest the out-of-plane wall to collapse into the building. | 1/9: B1029.201a - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 24 ft. 2/9: B1029.201b - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 27 ft. 3/9: B1029.201c - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 30 ft. 4/9: B1029.202a - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 24 ft. 5/9: B1029.202b - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 27 ft. 6/9: B1029.202c - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 30 ft. 7/9: B1029.203a - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 24 ft. 8/9: B1029.203b - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 27 ft. 9/9: B1029.203c - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 30 ft. | (all): Connections fail at one to several bays near the in-plane walls causing the bay nearest the out-of-plane wall to collapse into the building. | (all): Demo the fallen diaphragm as well was the surrounding diaphragm damaged. Replace the damaged diaphragm, oop wall connections. | 1 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1029\.2\w+ | Out-of-plane wall to diaphragm connection for Tilt-Up Roof Systems | Structural | Roof | OOP Conn | Connections fail along an entire wall line precipitating collapse of the wall outward and the diaphragm to the floor of the building. | 1/9: B1029.201a - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 24 ft. 2/9: B1029.201b - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 27 ft. 3/9: B1029.201c - Out-of-plane wall to diaphragm connection,bay spacing 25 ft., wall 30 ft. 4/9: B1029.202a - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 24 ft. 5/9: B1029.202b - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 27 ft. 6/9: B1029.202c - Out-of-plane wall to diaphragm connection,bay spacing 35 ft., wall 30 ft. 7/9: B1029.203a - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 24 ft. 8/9: B1029.203b - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 27 ft. 9/9: B1029.203c - Out-of-plane wall to diaphragm connection,bay spacing 50 ft., wall 30 ft. | (all): Connections fail along an entire wall line precipitating collapse of the wall outward and the diaphragm to the floor of the building. | (all): Demo the fallen wall and diaphragm as well as surrounding damaged components. | 2 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1031\.00\w+ | Bolted Shear Tab gravity connections for Steel Columns | Structural | Steel | Gravity | Yielding of shear tab and elongation of bolt holes, possible crack initiation around bolt holes or at shear tab weld. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | 1/1: B1031.001 - Bolted shear tab gravity connections | (all): Yielding of shear tab and elongation of bolt holes, possible crack initiation around bolt holes or at shear tab weld. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | (all): Careful inspection and welded repair to any cracks and possible replacement of shear tab if bolt hole deformations are excessive (possible for deeper 6-bolt or deeper shear tabs). Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1031\.00\w+ | Bolted Shear Tab gravity connections for Steel Columns | Structural | Steel | Gravity | Yielding of shear tab and elongation of bolt holes, possible crack initiation around bolt holes or at shear tab weld. | 1/1: B1031.001 - Bolted shear tab gravity connections | (all): Yielding of shear tab and elongation of bolt holes, possible crack initiation around bolt holes or at shear tab weld. | (all): Careful inspection and welded repair to any cracks and possible replacement of shear tab if bolt hole deformations are excessive (possible for deeper 6-bolt or deeper shear tabs). | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | full | 1
1 | B1031\.00\w+ | Bolted Shear Tab gravity connections for Steel Columns | Structural | Steel | Gravity | Partial tearing of shear tab and possibility of bolt shear failure (6-bolt or deeper connections). | 1/1: B1031.001 - Bolted shear tab gravity connections | (all): Partial tearing of shear tab and possibility of bolt shear failure (6-bolt or deeper connections). | (all): Repairs will include either welded repair of shear tab or possible complete replacement of shear tab and installation of new bolts. Repairs may require shoring of beam. | 2 | NA | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | bay | 6 | 1 | 21 | 1 | full | 1
1 | B1031\.00\w+ | Bolted Shear Tab gravity connections for Steel Columns | Structural | Steel | Gravity | Complete separation of shear tab, close to complete loss of vertical load resistance. | 1/1: B1031.001 - Bolted shear tab gravity connections | (all): Complete separation of shear tab, close to complete loss of vertical load resistance. | (all): Repair will include complete replacement of shear tab and installation of new bolts. Repairs will require shoring of beam. | 3 | NA | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | bay | 6 | 1 | 21 | 1 | full | 1
0 | B1031\.01\w+ | Steel Column Base Plates | Structural | Steel | Base Plates | Initiation of crack at the fusion line between the column flange and the base plate weld. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | 1/3: B1031.011a - Steel Column Base Plates, Column W < 150 plf 2/3: B1031.011b - Steel Column Base Plates, Column 150 plf < W < 300 plf 3/3: B1031.011c - Steel Column Base Plates, Column W > 300 plf | (all): Initiation of crack at the fusion line between the column flange and the base plate weld. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | (all): The repair will involve removal of a portion of grade slab, gouging out material surrounding the fracture initiating and re-welding, then repair of slab. Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1031\.01\w+ | Steel Column Base Plates | Structural | Steel | Base Plates | Initiation of crack at the fusion line between the column flange and the base plate weld. | 1/3: B1031.011a - Steel Column Base Plates, Column W < 150 plf 2/3: B1031.011b - Steel Column Base Plates, Column 150 plf < W < 300 plf 3/3: B1031.011c - Steel Column Base Plates, Column W > 300 plf | (all): Initiation of crack at the fusion line between the column flange and the base plate weld. | (all): The repair will involve removal of a portion of grade slab, gouging out material surrounding the fracture initiating and re-welding, then repair of slab. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1031\.01\w+ | Steel Column Base Plates | Structural | Steel | Base Plates | Propagation of brittle crack into column and/or base plate. | 1/3: B1031.011a - Steel Column Base Plates, Column W < 150 plf 2/3: B1031.011b - Steel Column Base Plates, Column 150 plf < W < 300 plf 3/3: B1031.011c - Steel Column Base Plates, Column W > 300 plf | (all): Propagation of brittle crack into column and/or base plate. | (all): Depending on the crack trajectory, the repair will range from replacement of a portion of the column or base plate to full replacement of the column base. Replacement will require shoring of column, torch cutting to remove damaged material, and fabrication and field welding to install replacement material. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1031\.01\w+ | Steel Column Base Plates | Structural | Steel | Base Plates | Complete fracture of the column (or column weld) and dislocation of column relative to the base. | 1/3: B1031.011a - Steel Column Base Plates, Column W < 150 plf 2/3: B1031.011b - Steel Column Base Plates, Column 150 plf < W < 300 plf 3/3: B1031.011c - Steel Column Base Plates, Column W > 300 plf | (all): Complete fracture of the column (or column weld) and dislocation of column relative to the base. | (all): Repair would likely involve replacing the entire base plate assembly and most of the column in the story above the base plate. | 3 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 1 | 21 | 1 | full | 1
1 | B1031\.02\w+ | Welded Column Splices | Structural | Steel | Splices | Ductile fracture of the groove weld flange splice. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | 1/3: B1031.021a - Welded column splices, Column W < 150 plf 2/3: B1031.021b - Welded column splices, Column 150 plf < W < 300 plf 3/3: B1031.021c - Welded column splices, Column W > 300 plf | (all): Ductile fracture of the groove weld flange splice. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | (all): Repair would involve gouging out the material adjacent to the fracture and repairing with a new groove weld. Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1031\.02\w+ | Welded Column Splices | Structural | Steel | Splices | Ductile fracture of the groove weld flange splice. | 1/3: B1031.021a - Welded column splices, Column W < 150 plf 2/3: B1031.021b - Welded column splices, Column 150 plf < W < 300 plf 3/3: B1031.021c - Welded column splices, Column W > 300 plf | (all): Ductile fracture of the groove weld flange splice. | (all): Repair would involve gouging out the material adjacent to the fracture and repairing with a new groove weld. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | full | 1
1 | B1031\.02\w+ | Welded Column Splices | Structural | Steel | Splices | DS1 followed by complete failure of the web splice plate and dislocation of the two column segments on either side of the splice. | 1/3: B1031.021a - Welded column splices, Column W < 150 plf 2/3: B1031.021b - Welded column splices, Column 150 plf < W < 300 plf 3/3: B1031.021c - Welded column splices, Column W > 300 plf | (all): DS1 followed by complete failure of the web splice plate and dislocation of the two column segments on either side of the splice. | (all): Repair may not be practically feasible, but would require either realignment or replacement of adjacent column segments and rewelding of splice. | 2 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 1 | 21 | 1 | full | 1
0 | B1033\.[12]\w+ | Buckling Restrained Steel Braces | Structural | Steel | Braces | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Severe loss of lateral resistance. | 1/138: B1033.101a - Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace < 40 plf. 2/138: B1033.101b - Steel Buckling Restrained Brace (BRB), Chevron brace, Weight of brace > 41 plf and < 99 plf. 3/138: B1033.101c - Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace > 100 plf. 4/138: B1033.111a - Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace < 40 plf. 5/138: B1033.111b - Steel Buckling Restrained Brace (BRB), Single Diagonal brace, Weight of brace > 41 plf and < 99 plf. 6/138: B1033.111c - Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace > 100 plf. 7/138: B1033.216a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 30ft. 8/138: B1033.216b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 30ft. 9/138: B1033.216c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 30ft. 10/138: B1033.216d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 14ft, Bay Width = 30ft. 11/138: B1033.215a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 30ft. 12/138: B1033.215b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 30ft. 13/138: B1033.215c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 30ft. 14/138: B1033.215d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 16ft, Bay Width = 30ft. 15/138: B1033.214a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 30ft. 16/138: B1033.214b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 30ft. 17/138: B1033.214c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 30ft. 18/138: B1033.214d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 20ft, Bay Width = 30ft. 19/138: B1033.213a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 20ft. 20/138: B1033.213b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 20ft. 21/138: B1033.213c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 20ft. 22/138: B1033.213d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 14ft, Bay Width = 20ft. 23/138: B1033.212a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 20ft. 24/138: B1033.212b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 20ft. 25/138: B1033.212c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 20ft. 26/138: B1033.212d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 16ft, Bay Width = 20ft. 27/138: B1033.211a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 20ft. 28/138: B1033.211b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 20ft. 29/138: B1033.211c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 20ft. 30/138: B1033.211d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 20ft, Bay Width = 20ft. 31/138: B1033.256a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 40ft. 32/138: B1033.256b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 40ft. 33/138: B1033.256c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 40ft. 34/138: B1033.256d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 14ft, Bay Width = 40ft. 35/138: B1033.255a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 40ft. 36/138: B1033.255b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 40ft. 37/138: B1033.255c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 40ft. 38/138: B1033.255d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 16ft, Bay Width = 40ft. 39/138: B1033.254a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 40ft. 40/138: B1033.254b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 40ft. 41/138: B1033.254c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 40ft. 42/138: B1033.254d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 20ft, Bay Width = 40ft. 43/138: B1033.253a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 30ft. 44/138: B1033.253b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 30ft. 45/138: B1033.253c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 30ft. 46/138: B1033.253d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 14ft, Bay Width = 30ft. 47/138: B1033.252a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 30ft. 48/138: B1033.252b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 30ft. 49/138: B1033.252c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 30ft. 50/138: B1033.252d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 16ft, Bay Width = 30ft. 51/138: B1033.251a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 30ft. 52/138: B1033.251b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 30ft. 53/138: B1033.251c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 30ft. 54/138: B1033.251d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Bolted Connection, Steel Core Area = 30in^2, Story Height = 20ft, Bay Width = 30ft. 55/138: B1033.226a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 30ft. 56/138: B1033.226b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 30ft. 57/138: B1033.226c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 30ft. 58/138: B1033.226d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 14ft, Bay Width = 30ft. 59/138: B1033.225a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 30ft. 60/138: B1033.225b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 30ft. 61/138: B1033.225c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 30ft. 62/138: B1033.225d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 16ft, Bay Width = 30ft. 63/138: B1033.224a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 30ft. 64/138: B1033.224b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 30ft. 65/138: B1033.224c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 30ft. 66/138: B1033.224d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 20ft, Bay Width = 30ft. 67/138: B1033.223a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 20ft. 68/138: B1033.223b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 20ft. 69/138: B1033.223c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 20ft. 70/138: B1033.223d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 14ft, Bay Width = 20ft. 71/138: B1033.222a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 20ft. 72/138: B1033.222b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 20ft. 73/138: B1033.222c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 20ft. 74/138: B1033.222d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 16ft, Bay Width = 20ft. 75/138: B1033.221a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 20ft. 76/138: B1033.221b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 20ft. 77/138: B1033.221c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 20ft. 78/138: B1033.221d - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 20ft, Bay Width = 20ft. 79/138: B1033.266a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 40ft. 80/138: B1033.266b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 40ft. 81/138: B1033.266c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 40ft. 82/138: B1033.266d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 14ft, Bay Width = 40ft. 83/138: B1033.265a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 40ft. 84/138: B1033.265b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 40ft. 85/138: B1033.265c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 40ft. 86/138: B1033.265d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 16ft, Bay Width = 40ft. 87/138: B1033.264a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 40ft. 88/138: B1033.264b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 40ft. 89/138: B1033.264c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 40ft. 90/138: B1033.264d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 20ft, Bay Width = 40ft. 91/138: B1033.263a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 30ft. 92/138: B1033.263b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 30ft. 93/138: B1033.263c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 30ft. 94/138: B1033.263d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 14ft, Bay Width = 30ft. 95/138: B1033.262a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 30ft. 96/138: B1033.262b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 30ft. 97/138: B1033.262c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 30ft. 98/138: B1033.262d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 16ft, Bay Width = 30ft. 99/138: B1033.261a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 30ft. 100/138: B1033.261b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 30ft. 101/138: B1033.261c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 30ft. 102/138: B1033.261d - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Pinned Connection, Steel Core Area = 30in^2, Story Height = 20ft, Bay Width = 30ft. 103/138: B1033.236a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 30ft. 104/138: B1033.236b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 30ft. 105/138: B1033.236c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 30ft. 106/138: B1033.235a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 30ft. 107/138: B1033.235b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 30ft. 108/138: B1033.235c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 30ft. 109/138: B1033.234a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 30ft. 110/138: B1033.234b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 30ft. 111/138: B1033.234c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 30ft. 112/138: B1033.233a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 20ft. 113/138: B1033.233b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 20ft. 114/138: B1033.233c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 20ft. 115/138: B1033.232a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 20ft. 116/138: B1033.232b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 20ft. 117/138: B1033.232c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 20ft. 118/138: B1033.231a - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 20ft. 119/138: B1033.231b - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 20ft. 120/138: B1033.231c - CoreBrace Buckling Restrained Brace (BRB), Diagonal Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 20ft. 121/138: B1033.276a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 40ft. 122/138: B1033.276b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 40ft. 123/138: B1033.276c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 40ft. 124/138: B1033.275a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 40ft. 125/138: B1033.275b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 40ft. 126/138: B1033.275c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 40ft. 127/138: B1033.274a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 40ft. 128/138: B1033.274b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 40ft. 129/138: B1033.274c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 40ft. 130/138: B1033.273a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 14ft, Bay Width = 30ft. 131/138: B1033.273b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 14ft, Bay Width = 30ft. 132/138: B1033.273c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 14ft, Bay Width = 30ft. 133/138: B1033.272a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 16ft, Bay Width = 30ft. 134/138: B1033.272b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 16ft, Bay Width = 30ft. 135/138: B1033.272c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 16ft, Bay Width = 30ft. 136/138: B1033.271a - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 5in^2, Story Height = 20ft, Bay Width = 30ft. 137/138: B1033.271b - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 10in^2, Story Height = 20ft, Bay Width = 30ft. 138/138: B1033.271c - CoreBrace Buckling Restrained Brace (BRB), Chevron Brace, Welded Connection, Steel Core Area = 20in^2, Story Height = 20ft, Bay Width = 30ft. | (all): Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Severe loss of lateral resistance. | (all): Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. | 1 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1033\.0([012]\w+¦33[abc]) | SCBF (WF Braces/HSS) | Structural | Steel | Braces | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | 1/30: B1033.001a - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF 2/30: B1033.001b - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/30: B1033.001c - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF 4/30: B1033.002a - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF 5/30: B1033.002b - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, 41 PLF < w < 99 PLF 6/30: B1033.002c - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF 7/30: B1033.003a - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w < 40 PLF 8/30: B1033.003b - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, 41 PLF < w < 99 PLF 9/30: B1033.003c - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w > 100 PLF 10/30: B1033.011a - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF 11/30: B1033.011b - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF 12/30: B1033.011c - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF 13/30: B1033.012a - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF 14/30: B1033.012b - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 15/30: B1033.012c - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF 16/30: B1033.013a - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w < 40 PLF 17/30: B1033.013b - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace 41 PLF < w < 99 PLF 18/30: B1033.013c - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w > 100 PLF 19/30: B1033.021a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w < 40 PLF 20/30: B1033.021b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace 41 PLF < w < 99 PLF 21/30: B1033.021c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w > 100 PLF 22/30: B1033.022a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard Single Diagonal Brace, Brace w < 40 PLF 23/30: B1033.022b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 24/30: B1033.022c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace w > 100 PLF 25/30: B1033.023a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w < 40 PLF 26/30: B1033.023b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace 41 PLF < w < 99 PLF 27/30: B1033.023c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w > 100 PLF 28/30: B1033.033a - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w < 40 PLF 29/30: B1033.033b - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace 41 PLF < w < 99 PLF 30/30: B1033.033c - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w > 100 PLF | (all): Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | (all): Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1033\.0([012]\w+¦33[abc]) | SCBF (WF Braces/HSS) | Structural | Steel | Braces | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | 1/30: B1033.001a - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF 2/30: B1033.001b - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/30: B1033.001c - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF 4/30: B1033.002a - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF 5/30: B1033.002b - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, 41 PLF < w < 99 PLF 6/30: B1033.002c - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF 7/30: B1033.003a - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w < 40 PLF 8/30: B1033.003b - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, 41 PLF < w < 99 PLF 9/30: B1033.003c - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w > 100 PLF 10/30: B1033.011a - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF 11/30: B1033.011b - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF 12/30: B1033.011c - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF 13/30: B1033.012a - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF 14/30: B1033.012b - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 15/30: B1033.012c - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF 16/30: B1033.013a - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w < 40 PLF 17/30: B1033.013b - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace 41 PLF < w < 99 PLF 18/30: B1033.013c - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w > 100 PLF 19/30: B1033.021a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w < 40 PLF 20/30: B1033.021b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace 41 PLF < w < 99 PLF 21/30: B1033.021c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w > 100 PLF 22/30: B1033.022a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard Single Diagonal Brace, Brace w < 40 PLF 23/30: B1033.022b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 24/30: B1033.022c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace w > 100 PLF 25/30: B1033.023a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w < 40 PLF 26/30: B1033.023b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace 41 PLF < w < 99 PLF 27/30: B1033.023c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w > 100 PLF 28/30: B1033.033a - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w < 40 PLF 29/30: B1033.033b - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace 41 PLF < w < 99 PLF 30/30: B1033.033c - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w > 100 PLF | (all): Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | ~~~ 1-18,28-30 ~~~ Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. ~~~ 19-27 ~~~ Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1033\.0([012]\w+¦33[abc]) | SCBF (WF Braces/HSS) | Structural | Steel | Braces | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | 1/30: B1033.001a - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF 2/30: B1033.001b - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/30: B1033.001c - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF 4/30: B1033.002a - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF 5/30: B1033.002b - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, 41 PLF < w < 99 PLF 6/30: B1033.002c - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF 7/30: B1033.003a - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w < 40 PLF 8/30: B1033.003b - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, 41 PLF < w < 99 PLF 9/30: B1033.003c - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w > 100 PLF 10/30: B1033.011a - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF 11/30: B1033.011b - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF 12/30: B1033.011c - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF 13/30: B1033.012a - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF 14/30: B1033.012b - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 15/30: B1033.012c - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF 16/30: B1033.013a - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w < 40 PLF 17/30: B1033.013b - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace 41 PLF < w < 99 PLF 18/30: B1033.013c - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w > 100 PLF 19/30: B1033.021a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w < 40 PLF 20/30: B1033.021b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace 41 PLF < w < 99 PLF 21/30: B1033.021c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w > 100 PLF 22/30: B1033.022a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard Single Diagonal Brace, Brace w < 40 PLF 23/30: B1033.022b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 24/30: B1033.022c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace w > 100 PLF 25/30: B1033.023a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w < 40 PLF 26/30: B1033.023b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace 41 PLF < w < 99 PLF 27/30: B1033.023c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w > 100 PLF 28/30: B1033.033a - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w < 40 PLF 29/30: B1033.033b - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace 41 PLF < w < 99 PLF 30/30: B1033.033c - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w > 100 PLF | (all): Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | (all): Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1033\.0([012]\w+¦33[abc]) | SCBF (WF Braces/HSS) | Structural | Steel | Braces | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. | 1/30: B1033.001a - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF 2/30: B1033.001b - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/30: B1033.001c - Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF 4/30: B1033.002a - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF 5/30: B1033.002b - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, 41 PLF < w < 99 PLF 6/30: B1033.002c - Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF 7/30: B1033.003a - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w < 40 PLF 8/30: B1033.003b - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, 41 PLF < w < 99 PLF 9/30: B1033.003c - Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w > 100 PLF 10/30: B1033.011a - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF 11/30: B1033.011b - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF 12/30: B1033.011c - Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF 13/30: B1033.012a - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF 14/30: B1033.012b - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 15/30: B1033.012c - Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF 16/30: B1033.013a - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w < 40 PLF 17/30: B1033.013b - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace 41 PLF < w < 99 PLF 18/30: B1033.013c - Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w > 100 PLF 19/30: B1033.021a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w < 40 PLF 20/30: B1033.021b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace 41 PLF < w < 99 PLF 21/30: B1033.021c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w > 100 PLF 22/30: B1033.022a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard Single Diagonal Brace, Brace w < 40 PLF 23/30: B1033.022b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 24/30: B1033.022c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace w > 100 PLF 25/30: B1033.023a - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w < 40 PLF 26/30: B1033.023b - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace 41 PLF < w < 99 PLF 27/30: B1033.023c - Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w > 100 PLF 28/30: B1033.033a - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w < 40 PLF 29/30: B1033.033b - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace 41 PLF < w < 99 PLF 30/30: B1033.033c - Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w > 100 PLF | (all): Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. | (all): Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | 4 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1033\.03[1-2][a-c] | SCBF designed to AISC minimum standards | Structural | Steel | Braces | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | 1/6: B1033.031a - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w < 40 PLF 2/6: B1033.031b - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/6: B1033.031c - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w > 100 PLF 4/6: B1033.032a - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w < 40 PLF 5/6: B1033.032b - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/6: B1033.032c - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w > 100 PLF | (all): Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | (all): Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | 1 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1033\.03[1-2][a-c] | SCBF designed to AISC minimum standards | Structural | Steel | Braces | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | 1/6: B1033.031a - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w < 40 PLF 2/6: B1033.031b - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/6: B1033.031c - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w > 100 PLF 4/6: B1033.032a - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w < 40 PLF 5/6: B1033.032b - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/6: B1033.032c - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w > 100 PLF | (all): Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | (all): Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1033\.03[1-2][a-c] | SCBF designed to AISC minimum standards | Structural | Steel | Braces | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. | 1/6: B1033.031a - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w < 40 PLF 2/6: B1033.031b - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/6: B1033.031c - Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w > 100 PLF 4/6: B1033.032a - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w < 40 PLF 5/6: B1033.032b - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/6: B1033.032c - Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w > 100 PLF | (all): Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. | (all): Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1033\.04[1-3][a-c] | SCBF Double Angle Braces | Structural | Steel | Braces | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | 1/9: B1033.041a - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w < 40 PLF 2/9: B1033.041b - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/9: B1033.041c - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w > 100 PLF 4/9: B1033.042a - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.042b - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/9: B1033.042c - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.043a - Special Concentric Braced Frame w double angle braces, X Brace, Brace w < 40 PLF 8/9: B1033.043b - Special Concentric Braced Frame w double angle braces, X Brace, Brace 41 PLF < w < 99 PLF 9/9: B1033.043c - Special Concentric Braced Frame w double angle braces, X Brace, Brace w > 100 PLF | (all): Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | (all): Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1033\.04[1-3][a-c] | SCBF Double Angle Braces | Structural | Steel | Braces | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | 1/9: B1033.041a - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w < 40 PLF 2/9: B1033.041b - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/9: B1033.041c - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w > 100 PLF 4/9: B1033.042a - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.042b - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/9: B1033.042c - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.043a - Special Concentric Braced Frame w double angle braces, X Brace, Brace w < 40 PLF 8/9: B1033.043b - Special Concentric Braced Frame w double angle braces, X Brace, Brace 41 PLF < w < 99 PLF 9/9: B1033.043c - Special Concentric Braced Frame w double angle braces, X Brace, Brace w > 100 PLF | (all): Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | (all): Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1033\.04[1-3][a-c] | SCBF Double Angle Braces | Structural | Steel | Braces | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. | 1/9: B1033.041a - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w < 40 PLF 2/9: B1033.041b - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/9: B1033.041c - Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w > 100 PLF 4/9: B1033.042a - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.042b - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/9: B1033.042c - Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.043a - Special Concentric Braced Frame w double angle braces, X Brace, Brace w < 40 PLF 8/9: B1033.043b - Special Concentric Braced Frame w double angle braces, X Brace, Brace 41 PLF < w < 99 PLF 9/9: B1033.043c - Special Concentric Braced Frame w double angle braces, X Brace, Brace w > 100 PLF | (all): Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. | (all): Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1033\.05[1-3][a-c] | OCBF Compact Braces | Structural | Steel | Braces | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | 1/9: B1033.051a - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w < 40 PLF 2/9: B1033.051b - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w, 41 PLF < w < 99 PLF 3/9: B1033.051c - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w > 100 PLF 4/9: B1033.052a - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.052b - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w, 41 PLF < w < 99 PLF 6/9: B1033.052c - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.053a - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w < 40 PLF 8/9: B1033.053b - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w, 41 PLF < w < 99 PLF 9/9: B1033.053c - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w > 100 PLF | (all): Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | (all): Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1033\.05[1-3][a-c] | OCBF Compact Braces | Structural | Steel | Braces | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | 1/9: B1033.051a - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w < 40 PLF 2/9: B1033.051b - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w, 41 PLF < w < 99 PLF 3/9: B1033.051c - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w > 100 PLF 4/9: B1033.052a - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.052b - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w, 41 PLF < w < 99 PLF 6/9: B1033.052c - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.053a - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w < 40 PLF 8/9: B1033.053b - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w, 41 PLF < w < 99 PLF 9/9: B1033.053c - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w > 100 PLF | (all): Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | (all): Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1033\.05[1-3][a-c] | OCBF Compact Braces | Structural | Steel | Braces | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. | 1/9: B1033.051a - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w < 40 PLF 2/9: B1033.051b - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w, 41 PLF < w < 99 PLF 3/9: B1033.051c - Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w > 100 PLF 4/9: B1033.052a - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.052b - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w, 41 PLF < w < 99 PLF 6/9: B1033.052c - Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.053a - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w < 40 PLF 8/9: B1033.053b - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w, 41 PLF < w < 99 PLF 9/9: B1033.053c - Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w > 100 PLF | (all): Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. | (all): Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1033\.06[1-3][a-c] | OCBF designed to ductile slenderness limits | Structural | Steel | Braces | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | 1/9: B1033.061a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w < 40 PLF 2/9: B1033.061b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/9: B1033.061c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w > 100 PLF 4/9: B1033.062a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.062b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/9: B1033.062c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.063a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w < 40 PLF 8/9: B1033.063b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace 41 PLF < w < 99 PLF 9/9: B1033.063c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w > 100 PLF | (all): Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | (all): Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | 1 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1033\.06[1-3][a-c] | OCBF designed to ductile slenderness limits | Structural | Steel | Braces | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | 1/9: B1033.061a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w < 40 PLF 2/9: B1033.061b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/9: B1033.061c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w > 100 PLF 4/9: B1033.062a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.062b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/9: B1033.062c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.063a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w < 40 PLF 8/9: B1033.063b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace 41 PLF < w < 99 PLF 9/9: B1033.063c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w > 100 PLF | (all): Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | (all): Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1033\.06[1-3][a-c] | OCBF designed to ductile slenderness limits | Structural | Steel | Braces | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. | 1/9: B1033.061a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w < 40 PLF 2/9: B1033.061b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace 41 PLF < w < 99 PLF 3/9: B1033.061c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w > 100 PLF 4/9: B1033.062a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.062b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF 6/9: B1033.062c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.063a - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w < 40 PLF 8/9: B1033.063b - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace 41 PLF < w < 99 PLF 9/9: B1033.063c - Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w > 100 PLF | (all): Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. | (all): Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1033\.07\w+ | Non Seismic Braces | Structural | Steel | Braces | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. | 1/9: B1033.071a - Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w < 40 PLF 2/9: B1033.071b - Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, 41 PLF < w < 99 PLF 3/9: B1033.071c - Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w > 100 PLF 4/9: B1033.072a - Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w < 40 PLF 5/9: B1033.072b - Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, 41 PLF < w < 99 PLF 6/9: B1033.072c - Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w > 100 PLF 7/9: B1033.073a - Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w < 40 PLF 8/9: B1033.073b - Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace 41 PLF < w < 99 PLF 9/9: B1033.073c - Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w > 100 PLF | (all): Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. | (all): Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. | 1 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1035\.0[0123]\w+ | Post Northridge Steel Beam Connection | Structural | Steel | Moment Connnections | Local beam flange and web buckling. | 1/8: B1035.001 - Post-Northridge RBS connection with welded web, beam one side of column only, beam depth <= W27 2/8: B1035.002 - Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 3/8: B1035.011 - Post-Northridge RBS connection with welded web, beams both sides of column, beam depth <= W27 4/8: B1035.012 - Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 5/8: B1035.021 - Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth <= W27 6/8: B1035.022 - Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth >= W30 7/8: B1035.031 - Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth <= W27 8/8: B1035.032 - Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth >= W30 | (all): Local beam flange and web buckling. | (all): The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1035\.0[0123]\w+ | Post Northridge Steel Beam Connection | Structural | Steel | Moment Connnections | DS1 plus lateral-torsional distortion of beam in hinge region. | 1/8: B1035.001 - Post-Northridge RBS connection with welded web, beam one side of column only, beam depth <= W27 2/8: B1035.002 - Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 3/8: B1035.011 - Post-Northridge RBS connection with welded web, beams both sides of column, beam depth <= W27 4/8: B1035.012 - Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 5/8: B1035.021 - Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth <= W27 6/8: B1035.022 - Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth >= W30 7/8: B1035.031 - Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth <= W27 8/8: B1035.032 - Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth >= W30 | (all): DS1 plus lateral-torsional distortion of beam in hinge region. | (all): Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1035\.0[0123]\w+ | Post Northridge Steel Beam Connection | Structural | Steel | Moment Connnections | Low-cycle fatigue fracture in buckled region of RBS. | 1/8: B1035.001 - Post-Northridge RBS connection with welded web, beam one side of column only, beam depth <= W27 2/8: B1035.002 - Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 3/8: B1035.011 - Post-Northridge RBS connection with welded web, beams both sides of column, beam depth <= W27 4/8: B1035.012 - Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 5/8: B1035.021 - Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth <= W27 6/8: B1035.022 - Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth >= W30 7/8: B1035.031 - Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth <= W27 8/8: B1035.032 - Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth >= W30 | (all): Low-cycle fatigue fracture in buckled region of RBS. | (all): Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1035\.0[45]\w+ | Pre-Northridge Steel Beam Connection | Structural | Steel | Moment Connnections | Fracture of lower beam flange weld and failure of web bolts (shear tab connection), with fractures confined to the weld region. | 1/4: B1035.041 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 2/4: B1035.042 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 3/4: B1035.051 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 4/4: B1035.052 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | (all): Fracture of lower beam flange weld and failure of web bolts (shear tab connection), with fractures confined to the weld region. | (all): Repair will typically require gouging out and re-welding of the beam flange weld, repair of shear tab, and replacing shear bolts. Repair and replace partitions at connection. | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | full | 1
0 | B1035\.0[45]\w+ | Pre-Northridge Steel Beam Connection | Structural | Steel | Moment Connnections | Similar to DS1, except that fracture propagates into column flanges. | 1/4: B1035.041 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 2/4: B1035.042 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 3/4: B1035.051 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 4/4: B1035.052 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | (all): Similar to DS1, except that fracture propagates into column flanges. | (all): In addition to column measures for DS1, repairs to column will be necessary. Cover plate, patch, or replace damaged column flange at connection. | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | full | 1
0 | B1035\.0[45]\w+ | Pre-Northridge Steel Beam Connection | Structural | Steel | Moment Connnections | Fracture of upper beam flange weld, without DS1 type damage. Fracture is confined to beam flange region. | 1/4: B1035.041 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 2/4: B1035.042 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 3/4: B1035.051 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 4/4: B1035.052 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | (all): Fracture of upper beam flange weld, without DS1 type damage. Fracture is confined to beam flange region. | (all): Repairs will be similar to those required for DS1, except that access to weld will likely require removal and replacement of a portion of the floor slab above the weld. | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1035\.0[45]\w+ | Pre-Northridge Steel Beam Connection | Structural | Steel | Moment Connnections | Similar to DS3, except that fracture propagates into column flanges. | 1/4: B1035.041 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 2/4: B1035.042 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 3/4: B1035.051 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 4/4: B1035.052 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | (all): Similar to DS3, except that fracture propagates into column flanges. | (all): In addition to column measures for DS3, repairs to column will be necessary that will involve replacing a portion of the column flange. | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1035\.0[45]\w+ | Pre-Northridge Steel Beam Connection | Structural | Steel | Moment Connnections | Fracture initiating at weld access hole and propagating through beam flange, possibly accompanied by local buckling deformations of web and flange. | 1/4: B1035.041 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 2/4: B1035.042 - Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 3/4: B1035.051 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 4/4: B1035.052 - Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | (all): Fracture initiating at weld access hole and propagating through beam flange, possibly accompanied by local buckling deformations of web and flange. | (all): Repair is similar to that for DS1 except that a portion of the beam web and flange may need to be heat straightened or replaced. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1035\.06\w+ | EBF Shear Link | Structural | Steel | Braces | Damage to concrete slab above the link beam. | 1/4: B1035.061a - EBF Shear Link, no floor beams, link w < 100 PLF 2/4: B1035.061b - EBF Shear Link, no floor beams, link w < 200 PLF 3/4: B1035.062a - EBF Shear Link, with floor beams, link w < 100 PLF 4/4: B1035.062b - EBF Shear Link, with floor beams, link w < 200 PLF | (all): Damage to concrete slab above the link beam. | (all): Replace concrete slab and finishes in 400 SF at EBF link. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1035\.06\w+ | EBF Shear Link | Structural | Steel | Braces | Web local buckling, flange local buckling. | 1/4: B1035.061a - EBF Shear Link, no floor beams, link w < 100 PLF 2/4: B1035.061b - EBF Shear Link, no floor beams, link w < 200 PLF 3/4: B1035.062a - EBF Shear Link, with floor beams, link w < 100 PLF 4/4: B1035.062b - EBF Shear Link, with floor beams, link w < 200 PLF | (all): Web local buckling, flange local buckling. | (all): Heat straightening of buckled elements. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1035\.06\w+ | EBF Shear Link | Structural | Steel | Braces | Initiation of fracture in the link beam and link flange. | 1/4: B1035.061a - EBF Shear Link, no floor beams, link w < 100 PLF 2/4: B1035.061b - EBF Shear Link, no floor beams, link w < 200 PLF 3/4: B1035.062a - EBF Shear Link, with floor beams, link w < 100 PLF 4/4: B1035.062b - EBF Shear Link, with floor beams, link w < 200 PLF | (all): Initiation of fracture in the link beam and link flange. | (all): Replace EBF link. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1041\.(0[358]\w+¦10\w+) | RC Column Connections OMF with beam failure | Structural | Concrete | Moment Connnections | Residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | 1/24: B1041.031a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side 2/24: B1041.031b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides 3/24: B1041.032a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side 4/24: B1041.032b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides 5/24: B1041.033a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side 6/24: B1041.033b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides 7/24: B1041.051a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam one side 8/24: B1041.051b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam both sides 9/24: B1041.052a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam one side 10/24: B1041.052b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam both sides 11/24: B1041.053a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam one side 12/24: B1041.053b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam both sides 13/24: B1041.081a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side 14/24: B1041.081b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides 15/24: B1041.082a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side 16/24: B1041.082b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides 17/24: B1041.083a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side 18/24: B1041.083b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides 19/24: B1041.101a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam one side 20/24: B1041.101b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam both sides 21/24: B1041.102a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam one side 22/24: B1041.102b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam both sides 23/24: B1041.103a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam one side 24/24: B1041.103b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | ~~~ 1-6,13-18 ~~~ Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. ~~~ 7-12,19-24 ~~~ Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1041\.(0[358]\w+¦10\w+) | RC Column Connections OMF with beam failure | Structural | Concrete | Moment Connnections | Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | 1/24: B1041.031a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side 2/24: B1041.031b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides 3/24: B1041.032a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side 4/24: B1041.032b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides 5/24: B1041.033a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side 6/24: B1041.033b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides 7/24: B1041.051a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam one side 8/24: B1041.051b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam both sides 9/24: B1041.052a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam one side 10/24: B1041.052b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam both sides 11/24: B1041.053a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam one side 12/24: B1041.053b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam both sides 13/24: B1041.081a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side 14/24: B1041.081b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides 15/24: B1041.082a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side 16/24: B1041.082b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides 17/24: B1041.083a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side 18/24: B1041.083b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides 19/24: B1041.101a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam one side 20/24: B1041.101b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam both sides 21/24: B1041.102a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam one side 22/24: B1041.102b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam both sides 23/24: B1041.103a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam one side 24/24: B1041.103b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | ~~~ 1-6,13-18 ~~~ Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. ~~~ 7-12,19-24 ~~~ Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1041\.(0[358]\w+¦10\w+) | RC Column Connections OMF with beam failure | Structural | Concrete | Moment Connnections | Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | 1/24: B1041.031a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side 2/24: B1041.031b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides 3/24: B1041.032a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side 4/24: B1041.032b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides 5/24: B1041.033a - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side 6/24: B1041.033b - ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides 7/24: B1041.051a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam one side 8/24: B1041.051b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam both sides 9/24: B1041.052a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam one side 10/24: B1041.052b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam both sides 11/24: B1041.053a - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam one side 12/24: B1041.053b - ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam both sides 13/24: B1041.081a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side 14/24: B1041.081b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides 15/24: B1041.082a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side 16/24: B1041.082b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides 17/24: B1041.083a - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side 18/24: B1041.083b - Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides 19/24: B1041.101a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam one side 20/24: B1041.101b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam both sides 21/24: B1041.102a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam one side 22/24: B1041.102b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam both sides 23/24: B1041.103a - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam one side 24/24: B1041.103b - Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | ~~~ 1-6 ~~~ Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. ~~~ 7-12,19-24 ~~~ Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. ~~~ 13-18 ~~~ Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement or column longitudinal reinforcement in the joint. Crushing of beam or joint core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1041\.(0[469]\w+¦11\w+) | RC Column Connections with Column Failure | Structural | Concrete | Moment Connnections | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | 1/24: B1041.041a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side 2/24: B1041.041b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides 3/24: B1041.042a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side 4/24: B1041.042b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides 5/24: B1041.043a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side 6/24: B1041.043b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides 7/24: B1041.061a - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam one side 8/24: B1041.061b - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam both sides 9/24: B1041.062a - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam one side 10/24: B1041.062b - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam both sides 11/24: B1041.063a - ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam one side 12/24: B1041.063b - ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam both sides 13/24: B1041.091a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side 14/24: B1041.091b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides 15/24: B1041.092a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side 16/24: B1041.092b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides 17/24: B1041.093a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side 18/24: B1041.093b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides 19/24: B1041.111a - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam one side 20/24: B1041.111b - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam both sides 21/24: B1041.112a - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam one side 22/24: B1041.112b - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam both sides 23/24: B1041.113a - Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam one side 24/24: B1041.113b - Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam both sides | ~~~ 1-6 ~~~ Concrete Cracking: beams, joints or possibly Residual concrete crack widths exceed 0.06 in. (1.5 mm). Column exhibit residual crack widths that require epoxy injection. ~~~ 7-24 ~~~ Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1041\.(0[469]\w+¦11\w+) | RC Column Connections with Column Failure | Structural | Concrete | Moment Connnections | Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | 1/24: B1041.041a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side 2/24: B1041.041b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides 3/24: B1041.042a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side 4/24: B1041.042b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides 5/24: B1041.043a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side 6/24: B1041.043b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides 7/24: B1041.061a - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam one side 8/24: B1041.061b - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam both sides 9/24: B1041.062a - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam one side 10/24: B1041.062b - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam both sides 11/24: B1041.063a - ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam one side 12/24: B1041.063b - ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam both sides 13/24: B1041.091a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side 14/24: B1041.091b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides 15/24: B1041.092a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side 16/24: B1041.092b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides 17/24: B1041.093a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side 18/24: B1041.093b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides 19/24: B1041.111a - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam one side 20/24: B1041.111b - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam both sides 21/24: B1041.112a - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam one side 22/24: B1041.112b - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam both sides 23/24: B1041.113a - Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam one side 24/24: B1041.113b - Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam both sides | ~~~ 1-6 ~~~ Concrete Spalling: slabs, beams, joints or possibly columns exhibit spalling of cover concrete that exposes transverse but not longitudinal reinforcing steel. Spalling of cover concrete possibly exposing transverse reinforcement. ~~~ 7-24 ~~~ Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1041\.(0[469]\w+¦11\w+) | RC Column Connections with Column Failure | Structural | Concrete | Moment Connnections | Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | 1/24: B1041.041a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side 2/24: B1041.041b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides 3/24: B1041.042a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side 4/24: B1041.042b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides 5/24: B1041.043a - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side 6/24: B1041.043b - ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides 7/24: B1041.061a - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam one side 8/24: B1041.061b - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam both sides 9/24: B1041.062a - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam one side 10/24: B1041.062b - ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam both sides 11/24: B1041.063a - ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam one side 12/24: B1041.063b - ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam both sides 13/24: B1041.091a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side 14/24: B1041.091b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides 15/24: B1041.092a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side 16/24: B1041.092b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides 17/24: B1041.093a - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side 18/24: B1041.093b - Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides 19/24: B1041.111a - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam one side 20/24: B1041.111b - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam both sides 21/24: B1041.112a - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam one side 22/24: B1041.112b - Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam both sides 23/24: B1041.113a - Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam one side 24/24: B1041.113b - Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam both sides | ~~~ 1-6 ~~~ Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement OR strength loss initiates in laboratory testing. exhibit concrete spalling that exposes longitudinal steel or crushing of core concrete. ~~~ 7-24 ~~~ Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | 3 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1041\.(07\w+¦1[23]\w+) | RC Column Connections with Column Failure w/ hign axial loads, or inadequate development | Structural | Concrete | Moment Connnections | Beams, columns or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | 1/18: B1041.071a - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam one side 2/18: B1041.071b - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam both sides 3/18: B1041.072a - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam one side 4/18: B1041.072b - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam both sides 5/18: B1041.073a - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam one side 6/18: B1041.073b - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam both sides 7/18: B1041.121a - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam both sides 8/18: B1041.121b - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam one side 9/18: B1041.122a - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam one side 10/18: B1041.122b - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam both sides 11/18: B1041.123a - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam one side 12/18: B1041.123b - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam both sides 13/18: B1041.131a - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam one side 14/18: B1041.131b - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam both sides 15/18: B1041.132a - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam one side 16/18: B1041.132b - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam both sides 17/18: B1041.133a - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam one side 18/18: B1041.133b - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam both sides | ~~~ 1-12 ~~~ Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. ~~~ 13-18 ~~~ Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1041\.(07\w+¦1[23]\w+) | RC Column Connections with Column Failure w/ hign axial loads, or inadequate development | Structural | Concrete | Moment Connnections | Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. | 1/18: B1041.071a - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam one side 2/18: B1041.071b - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam both sides 3/18: B1041.072a - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam one side 4/18: B1041.072b - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam both sides 5/18: B1041.073a - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam one side 6/18: B1041.073b - ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam both sides 7/18: B1041.121a - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam both sides 8/18: B1041.121b - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam one side 9/18: B1041.122a - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam one side 10/18: B1041.122b - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam both sides 11/18: B1041.123a - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam one side 12/18: B1041.123b - Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam both sides 13/18: B1041.131a - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam one side 14/18: B1041.131b - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam both sides 15/18: B1041.132a - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam one side 16/18: B1041.132b - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam both sides 17/18: B1041.133a - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam one side 18/18: B1041.133b - Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam both sides | ~~~ 1-12 ~~~ Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. ~~~ 13-18 ~~~ Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. | ~~~ 1-6 ~~~ Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). ~~~ 7-18 ~~~ Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | 2 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1041\.0[012]\w+ | RC Column Connections SMF or IMF | Structural | Concrete | Moment Connnections | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | 1/18: B1041.001a - ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam one side 2/18: B1041.001b - ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam both sides 3/18: B1041.002a - ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam one side 4/18: B1041.002b - ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam both sides 5/18: B1041.003a - ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam one side 6/18: B1041.003b - ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam both sides 7/18: B1041.011a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam one side 8/18: B1041.011b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam both sides 9/18: B1041.012a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam one side 10/18: B1041.012b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam both sides 11/18: B1041.013a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam one side 12/18: B1041.013b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam both sides 13/18: B1041.021a - ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam one side 14/18: B1041.021b - ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam both sides 15/18: B1041.022a - ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam one side 16/18: B1041.022b - ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam both sides 17/18: B1041.023a - ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam one side 18/18: B1041.023b - ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam both sides | (all): Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1041\.0[012]\w+ | RC Column Connections SMF or IMF | Structural | Concrete | Moment Connnections | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | 1/18: B1041.001a - ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam one side 2/18: B1041.001b - ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam both sides 3/18: B1041.002a - ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam one side 4/18: B1041.002b - ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam both sides 5/18: B1041.003a - ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam one side 6/18: B1041.003b - ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam both sides 7/18: B1041.011a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam one side 8/18: B1041.011b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam both sides 9/18: B1041.012a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam one side 10/18: B1041.012b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam both sides 11/18: B1041.013a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam one side 12/18: B1041.013b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam both sides 13/18: B1041.021a - ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam one side 14/18: B1041.021b - ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam both sides 15/18: B1041.022a - ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam one side 16/18: B1041.022b - ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam both sides 17/18: B1041.023a - ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam one side 18/18: B1041.023b - ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam both sides | (all): Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1041\.0[012]\w+ | RC Column Connections SMF or IMF | Structural | Concrete | Moment Connnections | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | 1/18: B1041.001a - ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam one side 2/18: B1041.001b - ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam both sides 3/18: B1041.002a - ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam one side 4/18: B1041.002b - ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam both sides 5/18: B1041.003a - ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam one side 6/18: B1041.003b - ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam both sides 7/18: B1041.011a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam one side 8/18: B1041.011b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam both sides 9/18: B1041.012a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam one side 10/18: B1041.012b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam both sides 11/18: B1041.013a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam one side 12/18: B1041.013b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam both sides 13/18: B1041.021a - ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam one side 14/18: B1041.021b - ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam both sides 15/18: B1041.022a - ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam one side 16/18: B1041.022b - ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam both sides 17/18: B1041.023a - ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam one side 18/18: B1041.023b - ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam both sides | (all): Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1041\.0[012]\w+ | RC Column Connections SMF or IMF | Structural | Concrete | Moment Connnections | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | 1/18: B1041.001a - ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam one side 2/18: B1041.001b - ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam both sides 3/18: B1041.002a - ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam one side 4/18: B1041.002b - ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam both sides 5/18: B1041.003a - ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam one side 6/18: B1041.003b - ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam both sides 7/18: B1041.011a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam one side 8/18: B1041.011b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam both sides 9/18: B1041.012a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam one side 10/18: B1041.012b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam both sides 11/18: B1041.013a - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam one side 12/18: B1041.013b - MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam both sides 13/18: B1041.021a - ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam one side 14/18: B1041.021b - ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam both sides 15/18: B1041.022a - ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam one side 16/18: B1041.022b - ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam both sides 17/18: B1041.023a - ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam one side 18/18: B1041.023b - ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam both sides | (all): Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | (all): Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | 3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1041\.5\w+ | Precast Hybrid Moment Frame | Structural | Concrete | Moment Connnections | Concrete Spalling: Beams or possibly joints exhibit spalling of cover concrete.. | 1/6: B1041.500a - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 24". 2/6: B1041.501a - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 36". 3/6: B1041.502a - ACI T1.2-03 PHMF, Conc Col & Bm = 36" x 36". 4/6: B1041.500b - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 24". Bare Frame 5/6: B1041.501b - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 36". Bare Frame 6/6: B1041.502b - ACI T1.2-03 PHMF, Conc Col & Bm = 36" x 36". Bare Frame | (all): Concrete Spalling: Beams or possibly joints exhibit spalling of cover concrete.. | ~~~ 1-3 ~~~ Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. ~~~ 4-6 ~~~ Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1041\.5\w+ | Precast Hybrid Moment Frame | Structural | Concrete | Moment Connnections | Continuity Bars Fracture: One or more mild steel continuity bars fracture in or near the region of the beam column interface such that the strength of the beam column element is decreased by 20%-25%. | 1/6: B1041.500a - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 24". 2/6: B1041.501a - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 36". 3/6: B1041.502a - ACI T1.2-03 PHMF, Conc Col & Bm = 36" x 36". 4/6: B1041.500b - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 24". Bare Frame 5/6: B1041.501b - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 36". Bare Frame 6/6: B1041.502b - ACI T1.2-03 PHMF, Conc Col & Bm = 36" x 36". Bare Frame | (all): Continuity Bars Fracture: One or more mild steel continuity bars fracture in or near the region of the beam column interface such that the strength of the beam column element is decreased by 20%-25%. | ~~~ 1-3 ~~~ Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Provide shoring and remove concrete necessary to access ruptured mild steel. Remove the mild steel leaving the core of the beam and the grout pad intact (this allows the PT stress to be maintained through the repair process). Core through the joint to remove the mild steel that passes through the joint. Replace mild steel through the joint and provide mechanical coupling to remaining bar anchored in beam. Pour concrete to place the mass spalled and chipped out. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. ~~~ 4-6 ~~~ Provide shoring and remove concrete necessary to access ruptured mild steel. Remove the mild steel leaving the core of the beam and the grout pad intact (this allows the PT stress to be maintained through the repair process). Core through the joint to remove the mild steel that passes through the joint. Replace mild steel through the joint and provide mechanical coupling to remaining bar anchored in beam. Pour concrete to place the mass spalled and chipped out. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1041\.5\w+ | Precast Hybrid Moment Frame | Structural | Concrete | Moment Connnections | Post Tension Cable Yields: The PT strand running through the beam-column section yields. This damage state will effect all similar fragilities between the PT tendon anchors. | 1/6: B1041.500a - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 24". 2/6: B1041.501a - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 36". 3/6: B1041.502a - ACI T1.2-03 PHMF, Conc Col & Bm = 36" x 36". 4/6: B1041.500b - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 24". Bare Frame 5/6: B1041.501b - ACI T1.2-03 PHMF, Conc Col & Bm = 24" x 36". Bare Frame 6/6: B1041.502b - ACI T1.2-03 PHMF, Conc Col & Bm = 36" x 36". Bare Frame | (all): Post Tension Cable Yields: The PT strand running through the beam-column section yields. This damage state will effect all similar fragilities between the PT tendon anchors. | ~~~ 1-3 ~~~ Remove end caps and determine the level of damage to the PT strand. Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Provide shoring and remove concrete necessary to access ruptured mild steel. Remove the mild steel leaving the core of the beam and the grout pad intact. Core through the joint to remove the mild steel that passes through the joint. Replace mild steel through the joint and provide mechanical coupling to remaining bar anchored in beam. Pour concrete to place the mass spalled and chipped out. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. If necessary replace PT strand, else re-tension PT strand to obtain the desired stress level. ~~~ 4-6 ~~~ Remove end caps and determine the level of damage to the PT strand. Clean area adjacent to the damaged concrete. Provide shoring and remove concrete necessary to access ruptured mild steel. Remove the mild steel leaving the core of the beam and the grout pad intact. Core through the joint to remove the mild steel that passes through the joint. Replace mild steel through the joint and provide mechanical coupling to remaining bar anchored in beam. Pour concrete to place the mass spalled and chipped out. If necessary replace PT strand, else re-tension PT strand to obtain the desired stress level. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1042\.\w+ | Concrete Link Beam | Structural | Concrete | Link Beam | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | 1/12: B1042.001a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" 2/12: B1042.001b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" 3/12: B1042.002a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" 4/12: B1042.002b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" 5/12: B1042.011a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" 6/12: B1042.011b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" 7/12: B1042.012a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" 8/12: B1042.012b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" 9/12: B1042.021a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" 10/12: B1042.021b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" 11/12: B1042.022a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" 12/12: B1042.022b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | (all): Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | (all): Epoxy inject cracks (200 to 240 inches in length). | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1042\.\w+ | Concrete Link Beam | Structural | Concrete | Link Beam | Residual cracks greater than 1/8 inch and minor spalling of concrete. | 1/12: B1042.001a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" 2/12: B1042.001b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" 3/12: B1042.002a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" 4/12: B1042.002b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" 5/12: B1042.011a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" 6/12: B1042.011b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" 7/12: B1042.012a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" 8/12: B1042.012b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" 9/12: B1042.021a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" 10/12: B1042.021b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" 11/12: B1042.022a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" 12/12: B1042.022b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | (all): Residual cracks greater than 1/8 inch and minor spalling of concrete. | (all): Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1042\.\w+ | Concrete Link Beam | Structural | Concrete | Link Beam | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. | 1/12: B1042.001a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" 2/12: B1042.001b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" 3/12: B1042.002a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" 4/12: B1042.002b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" 5/12: B1042.011a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" 6/12: B1042.011b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" 7/12: B1042.012a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" 8/12: B1042.012b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" 9/12: B1042.021a - Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" 10/12: B1042.021b - Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" 11/12: B1042.022a - Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" 12/12: B1042.022b - Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | (all): Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. | (all): Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. | 3 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1044\.(09\w+¦1[01]\w+) | RC Shear Walls: Flexure Controlled | Structural | Concrete | Shear Walls | Spalling of cover, vertical cracks greater than 1/16 inch. | 1/9: B1044.091 - Slender Concrete Wall, 12" thick, 12' high, 15' long 2/9: B1044.092 - Slender Concrete Wall, 12" thick, 12' high, 20' long 3/9: B1044.093 - Slender Concrete Wall, 12" thick, 12' high, 30' long 4/9: B1044.101 - Slender Concrete Wall, 18" thick, 12' high, 15' long 5/9: B1044.102 - Slender Concrete Wall, 18" thick, 12' high, 20' long 6/9: B1044.103 - Slender Concrete Wall, 18" thick, 12' high, 30' long 7/9: B1044.111 - Slender Concrete Wall, 30" thick, 12' high, 15' long 8/9: B1044.112 - Slender Concrete Wall, 30" thick, 12' high, 20' long 9/9: B1044.113 - Slender Concrete Wall, 30" thick, 12' high, 30' long | (all): Spalling of cover, vertical cracks greater than 1/16 inch. | (all): Epoxy inject cracks and patch spalled concrete. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1044\.(09\w+¦1[01]\w+) | RC Shear Walls: Flexure Controlled | Structural | Concrete | Shear Walls | Exposed longitudinal reinforcing. | 1/9: B1044.091 - Slender Concrete Wall, 12" thick, 12' high, 15' long 2/9: B1044.092 - Slender Concrete Wall, 12" thick, 12' high, 20' long 3/9: B1044.093 - Slender Concrete Wall, 12" thick, 12' high, 30' long 4/9: B1044.101 - Slender Concrete Wall, 18" thick, 12' high, 15' long 5/9: B1044.102 - Slender Concrete Wall, 18" thick, 12' high, 20' long 6/9: B1044.103 - Slender Concrete Wall, 18" thick, 12' high, 30' long 7/9: B1044.111 - Slender Concrete Wall, 30" thick, 12' high, 15' long 8/9: B1044.112 - Slender Concrete Wall, 30" thick, 12' high, 20' long 9/9: B1044.113 - Slender Concrete Wall, 30" thick, 12' high, 30' long | (all): Exposed longitudinal reinforcing. | (all): Shore wall, remove all concrete in damaged regions, replace concrete. | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1044\.(09\w+¦1[01]\w+) | RC Shear Walls: Flexure Controlled | Structural | Concrete | Shear Walls | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip | 1/9: B1044.091 - Slender Concrete Wall, 12" thick, 12' high, 15' long 2/9: B1044.092 - Slender Concrete Wall, 12" thick, 12' high, 20' long 3/9: B1044.093 - Slender Concrete Wall, 12" thick, 12' high, 30' long 4/9: B1044.101 - Slender Concrete Wall, 18" thick, 12' high, 15' long 5/9: B1044.102 - Slender Concrete Wall, 18" thick, 12' high, 20' long 6/9: B1044.103 - Slender Concrete Wall, 18" thick, 12' high, 30' long 7/9: B1044.111 - Slender Concrete Wall, 30" thick, 12' high, 15' long 8/9: B1044.112 - Slender Concrete Wall, 30" thick, 12' high, 20' long 9/9: B1044.113 - Slender Concrete Wall, 30" thick, 12' high, 30' long | (all): Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip | (all): Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 21 | 1 | full | 1
1 | B1044\.0[012]\w+ | RC Shear Walls: Shear Controlled, Rectangular | Structural | Concrete | Shear Walls | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | 1/9: B1044.001 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain up to 15' high 2/9: B1044.002 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain 16' high to 24' high 3/9: B1044.003 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain 25' high to 40' high 4/9: B1044.011 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of up to 15' 5/9: B1044.012 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 16' to 24' 6/9: B1044.013 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 24' to 40' 7/9: B1044.021 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights up to 15' 8/9: B1044.022 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 16' - 24' 9/9: B1044.023 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 25' - 40' | (all): Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | (all): Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1044\.0[012]\w+ | RC Shear Walls: Shear Controlled, Rectangular | Structural | Concrete | Shear Walls | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | 1/9: B1044.001 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain up to 15' high 2/9: B1044.002 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain 16' high to 24' high 3/9: B1044.003 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain 25' high to 40' high 4/9: B1044.011 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of up to 15' 5/9: B1044.012 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 16' to 24' 6/9: B1044.013 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 24' to 40' 7/9: B1044.021 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights up to 15' 8/9: B1044.022 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 16' - 24' 9/9: B1044.023 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 25' - 40' | (all): Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | (all): (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
1 | B1044\.0[012]\w+ | RC Shear Walls: Shear Controlled, Rectangular | Structural | Concrete | Shear Walls | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. | 1/9: B1044.001 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain up to 15' high 2/9: B1044.002 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain 16' high to 24' high 3/9: B1044.003 - Rectangular low aspect ratio concrete walls 8" or less thick single curtain 25' high to 40' high 4/9: B1044.011 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of up to 15' 5/9: B1044.012 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 16' to 24' 6/9: B1044.013 - Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 24' to 40' 7/9: B1044.021 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights up to 15' 8/9: B1044.022 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 16' - 24' 9/9: B1044.023 - Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 25' - 40' | (all): Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. | (all): (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 0 | 0 | 0 | full | 1
0 | B1044\.0[345678]\w+ | RC Shear Walls: Shear Controlled, With Return Flanges or Boundary Columns | Structural | Concrete | Shear Walls | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | 1/18: B1044.031 - Low-rise reinforced concrete walls with return flanges, less than 8" thick up to 15' high 2/18: B1044.032 - Low-rise reinforced concrete walls with return flanges, less than 8" thick, 16' to 24' high 3/18: B1044.033 - Low-rise reinforced concrete walls with return flanges, less than 8" thick, 25' to 40' high 4/18: B1044.041 - Low-rise reinforced concrete walls with return flanges, 8" to 16" thick up to 15' high 5/18: B1044.042 - Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 16' to 24' high 6/18: B1044.043 - Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 25' to 40' high 7/18: B1044.051 - Low-rise reinforced concrete walls with return flanges, 17" to 24" thick" up to 15' high 8/18: B1044.052 - Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 16' to 24' high 9/18: B1044.053 - Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 25' to 40' high 10/18: B1044.061 - Low rise reinforced concrete walls with boundary columns, less than 8" thick, height <15' 11/18: B1044.062 - Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 16'-24' 12/18: B1044.063 - Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 24'-40' 13/18: B1044.071 - Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height <15' 14/18: B1044.072 - Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 16'-24' 15/18: B1044.073 - Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 24'-40' 16/18: B1044.081 - Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height <15' 17/18: B1044.082 - Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 16'-24' 18/18: B1044.083 - Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 24'-40' | (all): Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | (all): Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | 1 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
0 | B1044\.0[345678]\w+ | RC Shear Walls: Shear Controlled, With Return Flanges or Boundary Columns | Structural | Concrete | Shear Walls | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. | 1/18: B1044.031 - Low-rise reinforced concrete walls with return flanges, less than 8" thick up to 15' high 2/18: B1044.032 - Low-rise reinforced concrete walls with return flanges, less than 8" thick, 16' to 24' high 3/18: B1044.033 - Low-rise reinforced concrete walls with return flanges, less than 8" thick, 25' to 40' high 4/18: B1044.041 - Low-rise reinforced concrete walls with return flanges, 8" to 16" thick up to 15' high 5/18: B1044.042 - Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 16' to 24' high 6/18: B1044.043 - Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 25' to 40' high 7/18: B1044.051 - Low-rise reinforced concrete walls with return flanges, 17" to 24" thick" up to 15' high 8/18: B1044.052 - Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 16' to 24' high 9/18: B1044.053 - Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 25' to 40' high 10/18: B1044.061 - Low rise reinforced concrete walls with boundary columns, less than 8" thick, height <15' 11/18: B1044.062 - Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 16'-24' 12/18: B1044.063 - Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 24'-40' 13/18: B1044.071 - Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height <15' 14/18: B1044.072 - Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 16'-24' 15/18: B1044.073 - Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 24'-40' 16/18: B1044.081 - Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height <15' 17/18: B1044.082 - Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 16'-24' 18/18: B1044.083 - Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 24'-40' | (all): Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. | (all): (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 0 | 0 | 0 | full | 1
1 | B1044\.2\w+ | Precast Tilt up Panel | Structural | Concrete | Shear Walls | Residual Cracking requiring epoxy injection | 1/24: B1044.201a - Precast tilt-up panel, pre 1976, 6.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 20 ft. wide 2/24: B1044.202a - Precast tilt-up panel, pre 1976, 6.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 25 ft. wide 3/24: B1044.203a - Precast tilt-up panel, pre 1976, 6.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 30 ft. wide 4/24: B1044.201b - Precast tilt-up panel, pre 1976, 6.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 20 ft. wide 5/24: B1044.202b - Precast tilt-up panel, pre 1976, 6.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 25 ft. wide 6/24: B1044.203b - Precast tilt-up panel, pre 1976, 6.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 30 ft. wide 7/24: B1044.211a - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 20 ft. wide 8/24: B1044.212a - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 25 ft. wide 9/24: B1044.213a - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 30 ft. wide 10/24: B1044.211b - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 20 ft. wide 11/24: B1044.212b - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 25 ft. wide 12/24: B1044.213b - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 30 ft. wide 13/24: B1044.211c - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 30 ft. to roof with 3 ft. parapet above, 20 ft. wide 14/24: B1044.212c - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 30 ft. to roof with 3 ft. parapet above, 25 ft. wide 15/24: B1044.213c - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 30 ft. to roof with 3 ft. parapet above, 30 ft. wide 16/24: B1044.221a - Precast tilt-up panel, post 1996, 9.25 in. thick, 24 ft. to roof with 3 ft. parapet above, 20 ft. wide 17/24: B1044.222a - Precast tilt-up panel, post 1996, 9.25 in. thick, 24 ft. to roof with 3 ft. parapet above, 25 ft. wide 18/24: B1044.223a - Precast tilt-up panel, post 1996, 9.25 in. thick, 24 ft. to roof with 3 ft. parapet above, 30 ft. wide 19/24: B1044.221b - Precast tilt-up panel, post 1996, 9.25 in. thick, 27 ft. to roof with 3 ft. parapet above, 20 ft. wide 20/24: B1044.222b - Precast tilt-up panel, post 1996, 9.25 in. thick, 27 ft. to roof with 3 ft. parapet above, 25 ft. wide 21/24: B1044.223b - Precast tilt-up panel, post 1996, 9.25 in. thick, 27 ft. to roof with 3 ft. parapet above, 30 ft. wide 22/24: B1044.221c - Precast tilt-up panel, post 1996, 9.25 in. thick, 30 ft. to roof with 3 ft. parapet above, 20 ft. wide 23/24: B1044.222c - Precast tilt-up panel, post 1996, 9.25 in. thick, 30 ft. to roof with 3 ft. parapet above, 25 ft. wide 24/24: B1044.223c - Precast tilt-up panel, post 1996, 9.25 in. thick, 30 ft. to roof with 3 ft. parapet above, 30 ft. wide | (all): Residual Cracking requiring epoxy injection | (all): Epoxy inject residual cracks. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1044\.2\w+ | Precast Tilt up Panel | Structural | Concrete | Shear Walls | Damage State 1 + residual drift requiring realignment | 1/24: B1044.201a - Precast tilt-up panel, pre 1976, 6.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 20 ft. wide 2/24: B1044.202a - Precast tilt-up panel, pre 1976, 6.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 25 ft. wide 3/24: B1044.203a - Precast tilt-up panel, pre 1976, 6.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 30 ft. wide 4/24: B1044.201b - Precast tilt-up panel, pre 1976, 6.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 20 ft. wide 5/24: B1044.202b - Precast tilt-up panel, pre 1976, 6.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 25 ft. wide 6/24: B1044.203b - Precast tilt-up panel, pre 1976, 6.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 30 ft. wide 7/24: B1044.211a - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 20 ft. wide 8/24: B1044.212a - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 25 ft. wide 9/24: B1044.213a - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 24 ft. to roof with 3 ft. parapet above, 30 ft. wide 10/24: B1044.211b - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 20 ft. wide 11/24: B1044.212b - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 25 ft. wide 12/24: B1044.213b - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 27 ft. to roof with 3 ft. parapet above, 30 ft. wide 13/24: B1044.211c - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 30 ft. to roof with 3 ft. parapet above, 20 ft. wide 14/24: B1044.212c - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 30 ft. to roof with 3 ft. parapet above, 25 ft. wide 15/24: B1044.213c - Precast tilt-up panel, 1976 through 1996, 7.5 in. thick, 30 ft. to roof with 3 ft. parapet above, 30 ft. wide 16/24: B1044.221a - Precast tilt-up panel, post 1996, 9.25 in. thick, 24 ft. to roof with 3 ft. parapet above, 20 ft. wide 17/24: B1044.222a - Precast tilt-up panel, post 1996, 9.25 in. thick, 24 ft. to roof with 3 ft. parapet above, 25 ft. wide 18/24: B1044.223a - Precast tilt-up panel, post 1996, 9.25 in. thick, 24 ft. to roof with 3 ft. parapet above, 30 ft. wide 19/24: B1044.221b - Precast tilt-up panel, post 1996, 9.25 in. thick, 27 ft. to roof with 3 ft. parapet above, 20 ft. wide 20/24: B1044.222b - Precast tilt-up panel, post 1996, 9.25 in. thick, 27 ft. to roof with 3 ft. parapet above, 25 ft. wide 21/24: B1044.223b - Precast tilt-up panel, post 1996, 9.25 in. thick, 27 ft. to roof with 3 ft. parapet above, 30 ft. wide 22/24: B1044.221c - Precast tilt-up panel, post 1996, 9.25 in. thick, 30 ft. to roof with 3 ft. parapet above, 20 ft. wide 23/24: B1044.222c - Precast tilt-up panel, post 1996, 9.25 in. thick, 30 ft. to roof with 3 ft. parapet above, 25 ft. wide 24/24: B1044.223c - Precast tilt-up panel, post 1996, 9.25 in. thick, 30 ft. to roof with 3 ft. parapet above, 30 ft. wide | (all): Damage State 1 + residual drift requiring realignment | (all): Straighten the wall or replace the panel. | 2 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1049\.0[13][12] | RC Slabs - columns with shear reinforcing | Structural | Concrete | Gravity | Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | 1/4: B1049.011 - Reinforced concrete flat slabs- columns with shear reinforcing (stirrups or headed studs) 0.2<Vg/Vo<0.4 2/4: B1049.012 - Reinforced concrete flat slabs- columns with shear reinforcing (stirrups or headed studs) 0.4<Vg/Vo<.6 3/4: B1049.031 - Post-tensioned concrete flat slabs- columns with shear reinforcing 0<Vg/Vo<.0.4 4/4: B1049.032 - Post-tensioned concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.0.6 | (all): Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | (all): Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1049\.0[13][12] | RC Slabs - columns with shear reinforcing | Structural | Concrete | Gravity | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. | 1/4: B1049.011 - Reinforced concrete flat slabs- columns with shear reinforcing (stirrups or headed studs) 0.2<Vg/Vo<0.4 2/4: B1049.012 - Reinforced concrete flat slabs- columns with shear reinforcing (stirrups or headed studs) 0.4<Vg/Vo<.6 3/4: B1049.031 - Post-tensioned concrete flat slabs- columns with shear reinforcing 0<Vg/Vo<.0.4 4/4: B1049.032 - Post-tensioned concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.0.6 | (all): Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. | ~~~ 1 ~~~ Prepare work area for epoxy injection, inject epoxy into 70 feet of crack (50 feet top, 20 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. ~~~ 2 ~~~ Prepare work area for epoxy injection, inject epoxy into 85 feet of crack (60 feet top, 25 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. ~~~ 3 ~~~ Prepare work area for epoxy injection, inject epoxy into 45 feet of crack (35 feet top, 10 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. ~~~ 4 ~~~ Prepare work area for epoxy injection, inject epoxy into 60 feet of crack (45 feet top, 15 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. | 2 | NA | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | bay | 6 | 1 | 21 | 1 | full | 1
1 | B1049\.\w+a | RC Slabs no continuity reinforcement | Structural | Concrete | Gravity | Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | 1/7: B1049.001a - Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, no continuity reinf 2/7: B1049.002a - Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, no continuity reinf 3/7: B1049.003a - Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, no continuity reinf 4/7: B1049.021a - Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, no continuity reinf 5/7: B1049.022a - Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, no continuity reinf 6/7: B1049.041a - Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, no continuity reinf 7/7: B1049.042a - Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, no continuity reinf | (all): Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | (all): Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1049\.\w+a | RC Slabs no continuity reinforcement | Structural | Concrete | Gravity | Punching occurs causing significant spalling of concrete. | 1/7: B1049.001a - Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, no continuity reinf 2/7: B1049.002a - Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, no continuity reinf 3/7: B1049.003a - Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, no continuity reinf 4/7: B1049.021a - Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, no continuity reinf 5/7: B1049.022a - Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, no continuity reinf 6/7: B1049.041a - Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, no continuity reinf 7/7: B1049.042a - Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, no continuity reinf | ~~~ 1-5 ~~~ Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. ~~~ 6-7 ~~~ Punching occurs causing significant spalling of concrete. | (all): Shore damaged area in the two stories below. Remove 100 square feet of concrete slab per column, preserving the slab reinforcement; lap splice 30 new 10 foot long rebar with existing rebar; place formwork; recast concrete slab; remove forms, replace and repair finishes; replace furnishings, ceilings, mechanical, electrical, and plumbing systems. Cracks wide enough to be grouted are included in the portion of slab to be demolished and recast. | 2 | NA | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | bay | 6 | 1 | 21 | 1 | full | 1
0 | B1049\.\w+b | RC Slabs with continuity reinforcement | Structural | Concrete | Gravity | Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | 1/7: B1049.001b - Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, with continuity reinf 2/7: B1049.002b - Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, with continuity reinf 3/7: B1049.003b - Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, with continuity reinf 4/7: B1049.021b - Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, with continuity reinf 5/7: B1049.022b - Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, with continuity reinf 6/7: B1049.041b - Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, with continuity reinf 7/7: B1049.042b - Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, with continuity reinf | (all): Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | (all): Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1049\.\w+b | RC Slabs with continuity reinforcement | Structural | Concrete | Gravity | Punching occurs causing significant spalling of concrete. | 1/7: B1049.001b - Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, with continuity reinf 2/7: B1049.002b - Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, with continuity reinf 3/7: B1049.003b - Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, with continuity reinf 4/7: B1049.021b - Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, with continuity reinf 5/7: B1049.022b - Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, with continuity reinf 6/7: B1049.041b - Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, with continuity reinf 7/7: B1049.042b - Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, with continuity reinf | ~~~ 1-5 ~~~ Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. ~~~ 6-7 ~~~ Punching occurs causing significant spalling of concrete. | ~~~ 1-2,5-6 ~~~ Prepare work area for epoxy injection, inject epoxy into 40 feet of crack (30 feet top, 10 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. ~~~ 3,7 ~~~ Prepare work area for epoxy injection, inject epoxy into 55 feet of crack (40 feet top, 15 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. ~~~ 4 ~~~ Prepare work area for epoxy injection, inject epoxy into 25 feet of crack (20 feet top, 5 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. | 2 | NA | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | bay | 6 | 1 | 21 | 1 | full | 1
1 | B1051\.0[012][12] | Special Masonry Walls: shear dominated | Structural | Masonry | Walls | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | 1/6: B1051.001 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, up to 12 foot tall 2/6: B1051.002 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, greater than 12 foot tall 3/6: B1051.011 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, up to 12 foot tall 4/6: B1051.012 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, greater than 12 foot tall 5/6: B1051.021 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 16" thick, up to 12 foot tall 6/6: B1051.022 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated,16"' thick, greater than 12 foot tall | (all): First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | (all): Grout wall. Epoxy injection. Paint each side. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1051\.0[012][12] | Special Masonry Walls: shear dominated | Structural | Masonry | Walls | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. | 1/6: B1051.001 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, up to 12 foot tall 2/6: B1051.002 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, greater than 12 foot tall 3/6: B1051.011 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, up to 12 foot tall 4/6: B1051.012 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, greater than 12 foot tall 5/6: B1051.021 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 16" thick, up to 12 foot tall 6/6: B1051.022 - Ordinary reinforced masonry walls with partially grouted cells, shear dominated,16"' thick, greater than 12 foot tall | (all): Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. | (all): Shore. Demolish existing wall. Construct new wall. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 0 | 0 | 0 | full | 1
0 | B1051\.0[012][34] | Special Masonry Walls: flexure dominated | Structural | Masonry | Walls | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | 1/6: B1051.003 - Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated up to 12' tall 2/6: B1051.004 - Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated greater than 12' tall 3/6: B1051.013 - Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated up to 12' tall 4/6: B1051.014 - Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall 5/6: B1051.023 - Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated up to 12' tall 6/6: B1051.024 - Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated greater than 12' tall | (all): A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | (all): Cosmetic repair. Patch cracks and paint each side. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1051\.0[012][34] | Special Masonry Walls: flexure dominated | Structural | Masonry | Walls | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | 1/6: B1051.003 - Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated up to 12' tall 2/6: B1051.004 - Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated greater than 12' tall 3/6: B1051.013 - Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated up to 12' tall 4/6: B1051.014 - Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall 5/6: B1051.023 - Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated up to 12' tall 6/6: B1051.024 - Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated greater than 12' tall | (all): Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | (all): Remove loose masonry. Patch spalls with non-shrink grout. Grout wall. Epoxy injection. Paint each side. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1051\.0[012][34] | Special Masonry Walls: flexure dominated | Structural | Masonry | Walls | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. | 1/6: B1051.003 - Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated up to 12' tall 2/6: B1051.004 - Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated greater than 12' tall 3/6: B1051.013 - Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated up to 12' tall 4/6: B1051.014 - Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall 5/6: B1051.023 - Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated up to 12' tall 6/6: B1051.024 - Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated greater than 12' tall | (all): Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. | (all): Shore. - Demolish existing wall. - Construct new wall. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 21 | 1 | full | 1
1 | B1052\.0[012][12] | Ordinary Masonry Walls: shear dominated | Structural | Masonry | Walls | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | 1/4: B1052.001 - Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, up t o12' tall 2/4: B1052.002 - Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, greater than 12' tall 3/4: B1052.011 - Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, up to 12' tall 4/4: B1052.012 - Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, greater than 12' tall | (all): First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | ~~~ 1-2 ~~~ Epoxy injection. Paint each side. ~~~ 3-4 ~~~ Epoxy injection at cracks. Paint each side. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1052\.0[012][12] | Ordinary Masonry Walls: shear dominated | Structural | Masonry | Walls | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. | 1/4: B1052.001 - Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, up t o12' tall 2/4: B1052.002 - Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, greater than 12' tall 3/4: B1052.011 - Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, up to 12' tall 4/4: B1052.012 - Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, greater than 12' tall | (all): Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. | (all): Shore. Demolish existing wall. Construct new wall. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 0 | 0 | 0 | full | 1
0 | B1052\.0[012][34] | Ordinary Masonry Walls: flexure dominated | Structural | Masonry | Walls | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | 1/4: B1052.003 - Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated up to 12' tall 2/4: B1052.004 - Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall 3/4: B1052.013 - Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated up to 12' tall 4/4: B1052.014 - Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated greater than 12' tall | (all): A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | (all): Cosmetic repair. Patch cracks and paint each side. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1052\.0[012][34] | Ordinary Masonry Walls: flexure dominated | Structural | Masonry | Walls | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | 1/4: B1052.003 - Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated up to 12' tall 2/4: B1052.004 - Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall 3/4: B1052.013 - Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated up to 12' tall 4/4: B1052.014 - Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated greater than 12' tall | (all): Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | (all): Epoxy injection to repair cracks. Remove loose masonry. Patch spalls with non-shrink grout. Paint each side. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1052\.0[012][34] | Ordinary Masonry Walls: flexure dominated | Structural | Masonry | Walls | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. | 1/4: B1052.003 - Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated up to 12' tall 2/4: B1052.004 - Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall 3/4: B1052.013 - Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated up to 12' tall 4/4: B1052.014 - Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated greater than 12' tall | (all): Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. | (all): Shore. - Demolish existing wall. - Construct new wall. | 3 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 21 | 1 | full | 1
1 | B1061\.001a | Cold Formed Steel Walls with wood structural panel sheathing | Structural | CFS | Walls | Sheathing faster pull through or tear out. (20% of fasteners.) | 1/1: B1061.001a - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | (all): Sheathing faster pull through or tear out. (20% of fasteners.) | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, tape and sand, repaint. | 1 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1061\.001a | Cold Formed Steel Walls with wood structural panel sheathing | Structural | CFS | Walls | Failure of structural panels. | 1/1: B1061.001a - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | (all): Failure of structural panels. | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace sheathing, replace gypsum wall board, tape and sand, repaint. | 2 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
1 | B1061\.001a | Cold Formed Steel Walls with wood structural panel sheathing | Structural | CFS | Walls | Failure of wall. | 1/1: B1061.001a - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | (all): Failure of wall. | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Provide shoring. Modify mechanical and electrical as required for repair work. Replace metal stud framing, boundary elements, sheathing, replace gypsum wall board, tape and sand, repaint. | 3 | NA | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B1061\.001b | Cold Formed Steel Walls with wood structural panel sheathing (heavy clad) | Structural | CFS | Walls | Sheathing faster pull through or tear out. (20% of fasteners.) | 1/1: B1061.001b - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | (all): Sheathing faster pull through or tear out. (20% of fasteners.) | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, stucco, tape and sand, repaint. | 1 | NA | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1061\.001b | Cold Formed Steel Walls with wood structural panel sheathing (heavy clad) | Structural | CFS | Walls | Failure of structural panels. | 1/1: B1061.001b - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | (all): Failure of structural panels. | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace sheathing, replace gypsum wall board, stucco, tape and sand, repaint. | 2 | NA | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | rapid | 0
0 | B1061\.001b | Cold Formed Steel Walls with wood structural panel sheathing (heavy clad) | Structural | CFS | Walls | Failure of wall. | 1/1: B1061.001b - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | (all): Failure of wall. | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Provide shoring. Modify mechanical and electrical as required for repair work. Replace metal stud framing, boundary elements, sheathing, replace gypsum wall board, stucco, tape and sand, repaint. | 3 | NA | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B1061\.011a | Cold Formed Steel Walls with flat strap X bracing | Structural | CFS | Walls | Local buckling of chord studs. | 1/1: B1061.011a - Cold formed steel walls with flat strap X-bracing, interior - gypsum board | (all): Local buckling of chord studs. | (all): Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, metal stud framing as needed, reinstall X bracing as required, tape and sand, repaint. | 1 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
1 | B1061\.011a | Cold Formed Steel Walls with flat strap X bracing | Structural | CFS | Walls | Failure of many framing members and collapse. | 1/1: B1061.011a - Cold formed steel walls with flat strap X-bracing, interior - gypsum board | (all): Failure of many framing members and collapse. | (all): Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, boundary elements, metal stud framing, install X bracing, tape and sand, repaint. | 2 | NA | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B1061\.011b | Cold Formed Steel Walls with flat strap X bracing (heavy clad) | Structural | CFS | Walls | Local buckling of chord studs. | 1/1: B1061.011b - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | (all): Local buckling of chord studs. | (all): Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, stucco, metal stud framing as needed, reinstall X bracing as required, tape and sand, repaint. | 1 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
0 | B1061\.011b | Cold Formed Steel Walls with flat strap X bracing (heavy clad) | Structural | CFS | Walls | Failure of many framing members and collapse. | 1/1: B1061.011b - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | (all): Failure of many framing members and collapse. | (all): Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, stucco, boundary elements, metal stud framing, install X bracing, tape and sand, repaint. | 2 | NA | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B1061\.021a | Cold Formed Steel Walls with 22 or 31 mil steel sheathing | Structural | CFS | Walls | Pull out of sheathing fasteners from studs. | 1/1: B1061.021a - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | (all): Pull out of sheathing fasteners from studs. | (all): Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, tape, sand, paint. | 1 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1061\.021a | Cold Formed Steel Walls with 22 or 31 mil steel sheathing | Structural | CFS | Walls | Buckling of steel sheathing. Buckling of framing members. | 1/1: B1061.021a - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | (all): Buckling of steel sheathing. Buckling of framing members. | (all): Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Install new sheathing, new metal stud framing as needed, replace gypsum wall board, tape, sand, paint. | 2 | NA | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B1061\.021b | Cold Formed Steel Walls with 22 or 31 mil steel sheathing (heavy clad) | Structural | CFS | Walls | Pull out of sheathing fasteners from studs. | 1/1: B1061.021b - Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | (all): Pull out of sheathing fasteners from studs. | (all): Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, stucco, tape, sand, paint. | 1 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1061\.021b | Cold Formed Steel Walls with 22 or 31 mil steel sheathing (heavy clad) | Structural | CFS | Walls | Buckling of steel sheathing. Buckling of framing members. | 1/1: B1061.021b - Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | (all): Buckling of steel sheathing. Buckling of framing members. | (all): Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Install new sheathing, new metal stud framing as needed, replace gypsum wall board, stucco,, tape, sand, paint. | 2 | NA | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B1071\.[02]3\w+ | Wood walls with diagonal let in bracing | Structural | WLF | Walls | Failure of diagonal bracing | 1/2: B1071.031 - Wood walls with diagonal let-in bracing 2/2: B1071.231 - Exterior Structural Wall - Wood walls with diagonal let-in bracing | ~~~ 1 ~~~ Failure of diagonal bracing. ~~~ 2 ~~~ Failure of diagonal bracing, damage to window and door surrounds from sheathing bearing. | (all): Remove and replace sheathing studs, plates and bracing and replace with new stud wall construction of plywood, hold-downs, etc. Provide shoring as required. | 1 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B1071\.00\w+ | Wood Framed Walls with strutural panel sheathing | Structural | WLF | Walls | Slight separation of sheathing or nails which come loose. | 1/2: B1071.001 - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs 2/2: B1071.002 - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | (all): Slight separation of sheathing or nails which come loose. | (all): Remove exterior pliable siding, replace loose nails, reinstall siding. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1071\.00\w+ | Wood Framed Walls with strutural panel sheathing | Structural | WLF | Walls | Permanent rotation of sheathing, tear out of nails or sheathing. | 1/2: B1071.001 - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs 2/2: B1071.002 - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | (all): Permanent rotation of sheathing, tear out of nails or sheathing. | (all): Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1071\.00\w+ | Wood Framed Walls with strutural panel sheathing | Structural | WLF | Walls | Fracture of studs, major sill plate cracking. | 1/2: B1071.001 - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs 2/2: B1071.002 - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace siding, sheathing, studs and plates. Provide shoring as required. | 3 | NA | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B1071\.01\w+ | Wood Framed Walls with strutural panel sheathing (heavy clad) | Structural | WLF | Walls | Cracking of stucco. | 1/2: B1071.012 - Light framed wood walls with structural panel sheathing, stucco, hold-downs 2/2: B1071.011 - Light framed wood walls with structural panel sheathing, stucco no hold-downs | (all): Cracking of stucco. | (all): Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1071\.01\w+ | Wood Framed Walls with strutural panel sheathing (heavy clad) | Structural | WLF | Walls | Spalling of stucco, separation of stucco and sheathing from studs. | 1/2: B1071.012 - Light framed wood walls with structural panel sheathing, stucco, hold-downs 2/2: B1071.011 - Light framed wood walls with structural panel sheathing, stucco no hold-downs | (all): Spalling of stucco, separation of stucco and sheathing from studs. | (all): Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | 2 | NA | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B1071\.01\w+ | Wood Framed Walls with strutural panel sheathing (heavy clad) | Structural | WLF | Walls | Fracture of studs, major sill plate cracking. | 1/2: B1071.012 - Light framed wood walls with structural panel sheathing, stucco, hold-downs 2/2: B1071.011 - Light framed wood walls with structural panel sheathing, stucco no hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace studs, plates, sheathing, and stucco. Shore as required. | 3 | NA | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B1071\.04\w+ | Wood wall with only gypsum | Structural | WLF | Walls | Screws pop-out, minor cracking of wall board, warping or cracking of tape. | 1/1: B1071.041 - Exterior Wall - Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | (all): Screws pop-out, minor cracking of wall board, warping or cracking of tape. | (all): Retape joints, paste and repaint both sides of full 100 foot length of wall board. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1071\.04\w+ | Wood wall with only gypsum | Structural | WLF | Walls | Moderate cracking or crushing of gypsum wall boards (typically in corners and in corners of openings). | 1/1: B1071.041 - Exterior Wall - Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | (all): Moderate cracking or crushing of gypsum wall boards (typically in corners and in corners of openings). | (all): Remove full 100 foot length of wall board (both sides), install new wall board (both sides), tape, paste and repaint. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
0 | B1071\.04\w+ | Wood wall with only gypsum | Structural | WLF | Walls | Significant cracking and/or crushing of gypsum wall boards- buckling of studs and tearing of tracks. | 1/1: B1071.041 - Exterior Wall - Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | (all): Significant cracking and/or crushing of gypsum wall boards- buckling of studs and tearing of tracks. | (all): Remove and replace full 100 foot length of metal stud wall, both sides of the gypsum wall board and any embedded utilities, and tape, paste and repaint. | 3 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B1071\.20\w+ | Exterior Walls: Wood Light Frame (structural) | Structural | WLF | Walls | Slight separation of sheathing or nails which come loose. | 1/2: B1071.201 - Exterior Structural Wall - Light framed wood walls with structural panel sheathing, no hold-downs 2/2: B1071.202 - Exterior Structural Wall - Light framed wood walls with structural panel sheathing, with hold-downs | (all): Slight separation of sheathing or nails which come loose. | (all): Remove exterior pliable siding, replace loose nails, reinstall siding. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1071\.20\w+ | Exterior Walls: Wood Light Frame (structural) | Structural | WLF | Walls | Permanent rotation of sheathing, tear out of nails or sheathing. | 1/2: B1071.201 - Exterior Structural Wall - Light framed wood walls with structural panel sheathing, no hold-downs 2/2: B1071.202 - Exterior Structural Wall - Light framed wood walls with structural panel sheathing, with hold-downs | (all): Permanent rotation of sheathing, tear out of nails or sheathing. | (all): Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | 2 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B1071\.20\w+ | Exterior Walls: Wood Light Frame (structural) | Structural | WLF | Walls | Fracture of studs, major sill plate cracking. | 1/2: B1071.201 - Exterior Structural Wall - Light framed wood walls with structural panel sheathing, no hold-downs 2/2: B1071.202 - Exterior Structural Wall - Light framed wood walls with structural panel sheathing, with hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace siding, sheathing, studs and plates. Provide shoring as required. | 3 | NA | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B1071\.21\w+ | Exterior Walls: Wood Light Frame, Stucco | Structural | WLF | Walls | Cracking of stucco. | 1/3: B1071.210 - Exterior Structural Wall - Light framed wood walls with stucco exterior, no panelized sheathing, no hold-downs 2/3: B1071.211 - Exterior Structural Wall - Light framed wood walls with stucco exterior, OSB structural sheathing, no hold-downs 3/3: B1071.212 - Exterior Structural Wall - Light framed wood walls with stucco exterior, OSB structural sheathing, with hold-downs | (all): Cracking of stucco. | (all): Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B1071\.21\w+ | Exterior Walls: Wood Light Frame, Stucco | Structural | WLF | Walls | Spalling of stucco, separation of stucco and sheathing from studs. | 1/3: B1071.210 - Exterior Structural Wall - Light framed wood walls with stucco exterior, no panelized sheathing, no hold-downs 2/3: B1071.211 - Exterior Structural Wall - Light framed wood walls with stucco exterior, OSB structural sheathing, no hold-downs 3/3: B1071.212 - Exterior Structural Wall - Light framed wood walls with stucco exterior, OSB structural sheathing, with hold-downs | (all): Spalling of stucco, separation of stucco and sheathing from studs. | (all): Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | 2 | NA | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B1071\.21\w+ | Exterior Walls: Wood Light Frame, Stucco | Structural | WLF | Walls | Fracture of studs, major sill plate cracking. | 1/3: B1071.210 - Exterior Structural Wall - Light framed wood walls with stucco exterior, no panelized sheathing, no hold-downs 2/3: B1071.211 - Exterior Structural Wall - Light framed wood walls with stucco exterior, OSB structural sheathing, no hold-downs 3/3: B1071.212 - Exterior Structural Wall - Light framed wood walls with stucco exterior, OSB structural sheathing, with hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace studs, plates, sheathing, and stucco. Shore as required. | 3 | NA | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B1071\.3\w+ | Interior Walls: Wood Light Frame | Structural | WLF | Walls | Cracking of paint over fasteners or joints. | 1/2: B1071.301 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, no hold-downs 2/2: B1071.302 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, with hold-downs | (all): Cracking of paint over fasteners or joints. | (all): Gypsum wallboard repaired by replacing the tape along the seam of two adjacent panels and local areas with popped fasteners, applying new joint compound, sanding, and repainting. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | B1071\.3\w+ | Interior Walls: Wood Light Frame | Structural | WLF | Walls | Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. | 1/2: B1071.301 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, no hold-downs 2/2: B1071.302 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, with hold-downs | (all): Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. | (all): Replace 25 feet of the affected panel along with the application of new tape, joint compound, followed by sanding and repainting. Studs are not damaged. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B1071\.3\w+ | Interior Walls: Wood Light Frame | Structural | WLF | Walls | Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard, but framing adjustments possible for this damage state. | 1/2: B1071.301 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, no hold-downs 2/2: B1071.302 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, with hold-downs | (all): Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard, but framing adjustments possible for this damage state. | (all): Replace 100 feet of the affected panel along with the application of new tape, joint compound, followed by sanding and repainting. Studs are not damaged. | 3 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | rapid | 0
1 | B1071\.3\w+ | Interior Walls: Wood Light Frame | Structural | WLF | Walls | Permanent rotation of sheathing, tear out of nails or sheathing. | 1/2: B1071.301 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, no hold-downs 2/2: B1071.302 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, with hold-downs | (all): Permanent rotation of sheathing, tear out of nails or sheathing. | (all): Remove interior finish, remove wood sheathing, install new sheathing, reinstall and finish interior material. | 4 | NA | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B1071\.3\w+ | Interior Walls: Wood Light Frame | Structural | WLF | Walls | Fracture of studs, major sill plate cracking. | 1/2: B1071.301 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, no hold-downs 2/2: B1071.302 - Interior Structural Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard on both sides, with hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace interior finish, sheathing, studs and plates. Provide shoring as required. | 5 | NA | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B2011\.(301¦401) | Exterior Walls: Wood Light Frame (non-sturcuural with siding) | Non-structural | Enclosure | WLF | Slight separation of sheathing or nails which come loose. | 1/2: B2011.401 - Exterior Wall - Light framed wood walls with exterior panelized sheathing (OSB) and horizontal wood siding, no hold-downs 2/2: B2011.301 - Exterior Wall - Light framed wood walls with exterior panelized plywood siding (T1-11), no hold-downs | (all): Slight separation of sheathing or nails which come loose. | (all): Remove exterior pliable siding, replace loose nails, reinstall siding. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B2011\.(301¦401) | Exterior Walls: Wood Light Frame (non-sturcuural with siding) | Non-structural | Enclosure | WLF | Permanent rotation of sheathing, tear out of nails or sheathing. | 1/2: B2011.401 - Exterior Wall - Light framed wood walls with exterior panelized sheathing (OSB) and horizontal wood siding, no hold-downs 2/2: B2011.301 - Exterior Wall - Light framed wood walls with exterior panelized plywood siding (T1-11), no hold-downs | (all): Permanent rotation of sheathing, tear out of nails or sheathing. | (all): Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
0 | B2011\.(301¦401) | Exterior Walls: Wood Light Frame (non-sturcuural with siding) | Non-structural | Enclosure | WLF | Fracture of studs, major sill plate cracking. | 1/2: B2011.401 - Exterior Wall - Light framed wood walls with exterior panelized sheathing (OSB) and horizontal wood siding, no hold-downs 2/2: B2011.301 - Exterior Wall - Light framed wood walls with exterior panelized plywood siding (T1-11), no hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace siding, sheathing, studs and plates. Provide shoring as required. | 3 | NA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B2011\.[12]31 | Exterior Wood walls with diagonal let in bracing | Non-structural | Enclosure | WLF | Failure of diagonal bracing. | 1/2: B2011.131 - Exterior Wall - Wood walls with diagonal let-in bracing 2/2: B2011.231 - Wood walls with horizontal wood siding | (all): Failure of diagonal bracing. | (all): Remove and replace sheathing studs, plates and bracing and replace with new stud wall construction of plywood, hold-downs, etc. Provide shoring as required. | 1 | NA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B2011\.0[12]1a | Exterior Walls: Cold Form Steel with X bracing or steel sheathing | Non-structural | Enclosure | CFS | ?? | 1/2: B2011.011a - Exterior Wall - Cold formed steel walls with flat strap X-bracing, interior - gypsum board 2/2: B2011.021a - Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | ~~~ 1 ~~~ Local buckling of chord studs. ~~~ 2 ~~~ Pull out of sheathing fasteners from studs. | ~~~ 1 ~~~ Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, metal stud framing as needed, reinstall X bracing as required, tape and sand, repaint. ~~~ 2 ~~~ Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, tape, sand, paint. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
0 | B2011\.0[12]1a | Exterior Walls: Cold Form Steel with X bracing or steel sheathing | Non-structural | Enclosure | CFS | ?? | 1/2: B2011.011a - Exterior Wall - Cold formed steel walls with flat strap X-bracing, interior - gypsum board 2/2: B2011.021a - Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | ~~~ 1 ~~~ Failure of many framing members and collapse. ~~~ 2 ~~~ Buckling of steel sheathing. Buckling of framing members. | ~~~ 1 ~~~ Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, boundary elements, metal stud framing, install X bracing, tape and sand, repaint. ~~~ 2 ~~~ Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Install new sheathing, new metal stud framing as needed, replace gypsum wall board, tape, sand, paint. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | rapid | 0
1 | B2011\.0[12]1b | Exterior Walls: Cold Form Steel with X bracing or steel sheathing (heavy clad) | Non-structural | Enclosure | CFS | ?? | 1/2: B2011.011b - Exterior Wall - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side 2/2: B2011.021b - Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | ~~~ 1 ~~~ Local buckling of chord studs. ~~~ 2 ~~~ Pull out of sheathing fasteners from studs. | ~~~ 1 ~~~ Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, stucco, metal stud framing as needed, reinstall X bracing as required, tape and sand, repaint. ~~~ 2 ~~~ Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, stucco, tape, sand, paint. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
1 | B2011\.0[12]1b | Exterior Walls: Cold Form Steel with X bracing or steel sheathing (heavy clad) | Non-structural | Enclosure | CFS | ?? | 1/2: B2011.011b - Exterior Wall - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side 2/2: B2011.021b - Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | ~~~ 1 ~~~ Failure of many framing members and collapse. ~~~ 2 ~~~ Buckling of steel sheathing. Buckling of framing members. | ~~~ 1 ~~~ Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, stucco, boundary elements, metal stud framing, install X bracing, tape and sand, repaint. ~~~ 2 ~~~ Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Install new sheathing, new metal stud framing as needed, replace gypsum wall board, stucco,, tape, sand, paint. | 2 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B2011\.001a | Exterior Walls: Cold Form Steel with wood sheathing | Non-structural | Enclosure | CFS | Sheathing faster pull through or tear out. (20% of fasteners.) | 1/1: B2011.001a - Exterior Wall - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | (all): Sheathing faster pull through or tear out. (20% of fasteners.) | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, tape and sand, repaint. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B2011\.001a | Exterior Walls: Cold Form Steel with wood sheathing | Non-structural | Enclosure | CFS | Failure of structural panels. | 1/1: B2011.001a - Exterior Wall - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | (all): Failure of structural panels. | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace sheathing, replace gypsum wall board, tape and sand, repaint. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
0 | B2011\.001a | Exterior Walls: Cold Form Steel with wood sheathing | Non-structural | Enclosure | CFS | Failure of wall. | 1/1: B2011.001a - Exterior Wall - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | (all): Failure of wall. | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Provide shoring. Modify mechanical and electrical as required for repair work. Replace metal stud framing, boundary elements, sheathing, replace gypsum wall board, tape and sand, repaint. | 3 | NA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B2011\.001b | Exterior Walls: Cold Form Steel with wood sheathing (heavy clad) | Non-structural | Enclosure | CFS | Sheathing faster pull through or tear out. (20% of fasteners.) | 1/1: B2011.001b - Exterior Wall - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | (all): Sheathing faster pull through or tear out. (20% of fasteners.) | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, stucco, tape and sand, repaint. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B2011\.001b | Exterior Walls: Cold Form Steel with wood sheathing (heavy clad) | Non-structural | Enclosure | CFS | Failure of structural panels. | 1/1: B2011.001b - Exterior Wall - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | (all): Failure of structural panels. | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace sheathing, replace gypsum wall board, stucco, tape and sand, repaint. | 2 | NA | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | rapid | 0
1 | B2011\.001b | Exterior Walls: Cold Form Steel with wood sheathing (heavy clad) | Non-structural | Enclosure | CFS | Failure of wall. | 1/1: B2011.001b - Exterior Wall - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | (all): Failure of wall. | (all): Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Provide shoring. Modify mechanical and electrical as required for repair work. Replace metal stud framing, boundary elements, sheathing, replace gypsum wall board, stucco, tape and sand, repaint. | 3 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B2011\.1(01¦21) | Exterior Walls: Wood Light Frame (non-sturctural) | Non-structural | Enclosure | WLF | Slight separation of sheathing or nails which come loose. | 1/2: B2011.101 - Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs 2/2: B2011.121 - Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | (all): Slight separation of sheathing or nails which come loose. | (all): Remove exterior pliable siding, replace loose nails, reinstall siding. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B2011\.1(01¦21) | Exterior Walls: Wood Light Frame (non-sturctural) | Non-structural | Enclosure | WLF | Permanent rotation of sheathing, tear out of nails or sheathing. | 1/2: B2011.101 - Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs 2/2: B2011.121 - Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | (all): Permanent rotation of sheathing, tear out of nails or sheathing. | (all): Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
0 | B2011\.1(01¦21) | Exterior Walls: Wood Light Frame (non-sturctural) | Non-structural | Enclosure | WLF | Fracture of studs, major sill plate cracking. | 1/2: B2011.101 - Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs 2/2: B2011.121 - Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace siding, sheathing, studs and plates. Provide shoring as required. | 3 | NA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B2011\.1(02¦11) | Exterior Walls: Wood Light Frame (heavy clad) | Non-structural | Enclosure | WLF | Cracking of stucco. | 1/2: B2011.102 - Exterior Wall - Light framed wood walls with structural panel sheathing, stucco, hold-downs 2/2: B2011.111 - Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | (all): Cracking of stucco. | (all): Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B2011\.1(02¦11) | Exterior Walls: Wood Light Frame (heavy clad) | Non-structural | Enclosure | WLF | Spalling of stucco, separation of stucco and sheathing from studs. | 1/2: B2011.102 - Exterior Wall - Light framed wood walls with structural panel sheathing, stucco, hold-downs 2/2: B2011.111 - Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | (all): Spalling of stucco, separation of stucco and sheathing from studs. | (all): Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | 2 | NA | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | rapid | 0
1 | B2011\.1(02¦11) | Exterior Walls: Wood Light Frame (heavy clad) | Non-structural | Enclosure | WLF | Fracture of studs, major sill plate cracking. | 1/2: B2011.102 - Exterior Wall - Light framed wood walls with structural panel sheathing, stucco, hold-downs 2/2: B2011.111 - Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace studs, plates, sheathing, and stucco. Shore as required. | 3 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B2011\.201a | Precast Concrete Panels In Plane | Non-structural | Enclosure | Cladding | Cladding units damaged by impact at corners at column covers. Damage in field is either attributed to natural edge chipping / damage, or is deemed to not warrant full repair. Repair assumes cosmetic chip patching. | 1/1: B2011.201a - Precast Concrete Panels 4.5 inches thick - in plane deformation | (all): Cladding units damaged by impact at corners at column covers. Damage in field is either attributed to natural edge chipping / damage, or is deemed to not warrant full repair. Repair assumes cosmetic chip patching. | (all): By User, Repair cost assumed to equal 20% of DS2. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | B2011\.201a | Precast Concrete Panels In Plane | Non-structural | Enclosure | Cladding | Cladding units damaged by impact at corners at column covers. | 1/1: B2011.201a - Precast Concrete Panels 4.5 inches thick - in plane deformation | (all): Cladding units damaged by impact at corners at column covers. | (all): By User, Cost listed assumed the replacement of the panel | 1 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 5 | 1 | 7 | 0 | full | 1
1 | B2011\.201b | Precast Concrete Panels OOP | Non-structural | Enclosure | Cladding | Cladding units damaged by out of plane anchorage failure. Unit requires replacement. | 1/1: B2011.201b - Precast Concrete Panels 4.5 inches thick - out of plane deformation | (all): Cladding units damaged by out of plane anchorage failure. Unit requires replacement. | (all): By User - Replace cladding panel. | 1 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 5 | 1 | 14 | 0 | full | 1
0 | B2011\.211 | Exterior Walls: Wood Light Frame (stucco, not sturctural) | Non-structural | Enclosure | WLF | Cracking of stucco. | 1/1: B2011.211 - Exterior Wall - Light framed wood walls with stucco exterior over structural panel sheathing, no hold-downs | (all): Cracking of stucco. | (all): Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B2011\.211 | Exterior Walls: Wood Light Frame (stucco, not sturctural) | Non-structural | Enclosure | WLF | Spalling of stucco, separation of stucco and sheathing from studs. | 1/1: B2011.211 - Exterior Wall - Light framed wood walls with stucco exterior over structural panel sheathing, no hold-downs | (all): Spalling of stucco, separation of stucco and sheathing from studs. | (all): Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | 2 | NA | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | rapid | 0
0 | B2011\.211 | Exterior Walls: Wood Light Frame (stucco, not sturctural) | Non-structural | Enclosure | WLF | Fracture of studs, major sill plate cracking. | 1/1: B2011.211 - Exterior Wall - Light framed wood walls with stucco exterior over structural panel sheathing, no hold-downs | (all): Fracture of studs, major sill plate cracking. | (all): Remove and replace studs, plates, sheathing, and stucco. Shore as required. | 3 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B2011\.3[246]1 | Cripple Walls: No Stucco | Structural | WLF | Cripple Wall | Slight separation of sheathing or nails which come loose. | 1/3: B2011.321 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 2ft cripple wall height, no hold-downs 2/3: B2011.341 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 4ft cripple wall height, no hold-downs 3/3: B2011.361 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 6ft cripple wall height, no hold-downs | (all): Slight separation of sheathing or nails which come loose. | (all): Remove exterior pliable siding, replace loose nails, reinstall siding. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B2011\.3[246]1 | Cripple Walls: No Stucco | Structural | WLF | Cripple Wall | Permanent rotation of sheathing, tear out of nails or sheathing. | 1/3: B2011.321 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 2ft cripple wall height, no hold-downs 2/3: B2011.341 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 4ft cripple wall height, no hold-downs 3/3: B2011.361 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 6ft cripple wall height, no hold-downs | (all): Permanent rotation of sheathing, tear out of nails or sheathing. | (all): Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | full | 1
1 | B2011\.3[246]1 | Cripple Walls: No Stucco | Structural | WLF | Cripple Wall | Delamination of sheathing, fracture of studs, sill plate damage possible. | 1/3: B2011.321 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 2ft cripple wall height, no hold-downs 2/3: B2011.341 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 4ft cripple wall height, no hold-downs 3/3: B2011.361 - Light framed wood cripple wall with T1-11 siding (8d @ 6"), 6ft cripple wall height, no hold-downs | (all): Delamination of sheathing, fracture of studs, sill plate damage possible. | (all): Remove and replace siding, sheathing, studs and plates. Provide shoring as required. | 3 | NA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B2011\.4[246]1 | Cripple Walls: Stucco | Structural | WLF | Cripple Wall | Cracking of stucco, especially at corners and openings (access and utility). | 1/3: B2011.421 - Light framed wood cripple wall with stucco exterior, 2ft cripple wall height, no hold-downs 2/3: B2011.441 - Light framed wood cripple wall with stucco exterior, 4ft cripple wall height, no hold-downs 3/3: B2011.461 - Light framed wood cripple wall with stucco exterior, 6ft cripple wall height, no hold-downs | (all): Cracking of stucco, especially at corners and openings (access and utility). | (all): Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
0 | B2011\.4[246]1 | Cripple Walls: Stucco | Structural | WLF | Cripple Wall | Spalling of stucco, significant cracking, onset of delamination of stucco from studs and bottom plate. | 1/3: B2011.421 - Light framed wood cripple wall with stucco exterior, 2ft cripple wall height, no hold-downs 2/3: B2011.441 - Light framed wood cripple wall with stucco exterior, 4ft cripple wall height, no hold-downs 3/3: B2011.461 - Light framed wood cripple wall with stucco exterior, 6ft cripple wall height, no hold-downs | (all): Spalling of stucco, significant cracking, onset of delamination of stucco from studs and bottom plate. | (all): Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 6 | 0 | 0 | 0 | rapid | 0
0 | B2011\.4[246]1 | Cripple Walls: Stucco | Structural | WLF | Cripple Wall | Delamination of stucco at studs and bottom plate. | 1/3: B2011.421 - Light framed wood cripple wall with stucco exterior, 2ft cripple wall height, no hold-downs 2/3: B2011.441 - Light framed wood cripple wall with stucco exterior, 4ft cripple wall height, no hold-downs 3/3: B2011.461 - Light framed wood cripple wall with stucco exterior, 6ft cripple wall height, no hold-downs | (all): Delamination of stucco at studs and bottom plate. | (all): Remove and replace studs, plates, sheathing, and stucco. Shore as required. | 3 | NA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B2011\.411 | Exterior Walls: Wood Light Frame (stucco, sturctural) | Structural | Enclosure | WLF | Cracking of stucco. | 1/1: B2011.411 - Exterior Wall - Light framed wood walls with stucco exterior, no structural panel sheathing, no hold-downs | (all): Cracking of stucco. | (all): Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | rapid | 0
1 | B2011\.411 | Exterior Walls: Wood Light Frame (stucco, sturctural) | Structural | Enclosure | WLF | Spalling of stucco near openings and corners, widespread cracking of stucco. | 1/1: B2011.411 - Exterior Wall - Light framed wood walls with stucco exterior, no structural panel sheathing, no hold-downs | (all): Spalling of stucco near openings and corners, widespread cracking of stucco. | (all): Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | 2 | NA | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | rapid | 0
1 | B2011\.411 | Exterior Walls: Wood Light Frame (stucco, sturctural) | Structural | Enclosure | WLF | Widespread spalling of stucco, delamination of stucco, framing connnections may be loosened. | 1/1: B2011.411 - Exterior Wall - Light framed wood walls with stucco exterior, no structural panel sheathing, no hold-downs | (all): Widespread spalling of stucco, delamination of stucco, framing connnections may be loosened. | (all): Remove and replace studs, plates, sheathing, and stucco. Shore as required. | 3 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
0 | B2011\.541 | Cripple Walls: Horizontal Siding | Structural | WLF | Cripple Wall | Failure of any bracing within framing, cripple wall will need replacement and stregthening. | 1/1: B2011.541 - Light framed wood cripple wall with horizontal wood siding, no hold-downs | (all): Failure of any bracing within framing, cripple wall will need replacement and stregthening. | (all): Remove and replace sheathing studs, plates and bracing and replace with new stud wall construction of plywood, hold-downs, etc. Provide shoring as required. | 1 | NA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 6 | 1 | 7 | 0 | full | 1
1 | B2022\.(0[179]\w+¦08[34]¦[12]\w+) | Curtain Walls (3DS) | Non-structural | Enclosure | Glazing | Gasket seal failure. | 1/8: B2022.011 - Midrise stick-built curtain wall, Config: Asymmetric insulating glass units (dual-pane, unequal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/2 in. (13 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 2/8: B2022.071 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 3/8: B2022.072 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.060 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 4/8: B2022.083 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 5/8: B2022.084 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 6/8: B2022.091 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 7/8: B2022.101 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1 in. (25 mm) HS IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 8/8: B2022.201 - Curtain Walls - Unitized curtain wall (also generic unitized curtain wall), Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHBTM SGTTM; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = Varies sealant = wet | (all): Gasket seal failure. | (all): Remove glass panel and replace damaged gaskets. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | B2022\.(0[179]\w+¦08[34]¦[12]\w+) | Curtain Walls (3DS) | Non-structural | Enclosure | Glazing | Glass cracking. | 1/8: B2022.011 - Midrise stick-built curtain wall, Config: Asymmetric insulating glass units (dual-pane, unequal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/2 in. (13 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 2/8: B2022.071 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 3/8: B2022.072 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.060 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 4/8: B2022.083 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 5/8: B2022.084 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 6/8: B2022.091 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 7/8: B2022.101 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1 in. (25 mm) HS IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 8/8: B2022.201 - Curtain Walls - Unitized curtain wall (also generic unitized curtain wall), Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHBTM SGTTM; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = Varies sealant = wet | (all): Glass cracking. | (all): Replace cracked glass panel. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | B2022\.(0[179]\w+¦08[34]¦[12]\w+) | Curtain Walls (3DS) | Non-structural | Enclosure | Glazing | Glass falls out. | 1/8: B2022.011 - Midrise stick-built curtain wall, Config: Asymmetric insulating glass units (dual-pane, unequal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/2 in. (13 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 2/8: B2022.071 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 3/8: B2022.072 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.060 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 4/8: B2022.083 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 5/8: B2022.084 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 6/8: B2022.091 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 7/8: B2022.101 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1 in. (25 mm) HS IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 8/8: B2022.201 - Curtain Walls - Unitized curtain wall (also generic unitized curtain wall), Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHBTM SGTTM; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = Varies sealant = wet | (all): Glass falls out. | (all): Replace cracked glass panel; cover exposure in meantime. | 3 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 5 | 1 | 3 | 0 | rapid | 0
0 | B2022\.0([023456]\w+¦8[12]) | Curtain Walls (2DS) | Non-structural | Enclosure | Glazing | Glass cracking. | 1/23: B2022.001 - Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 2/23: B2022.002 - Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Insulating Glass Units (dual pane), Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 3/23: B2022.021 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 4/23: B2022.022 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 5/23: B2022.023 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 6/23: B2022.031 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 7/23: B2022.032 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0 in. (0 mm); aspect ratio = 6:5 sealant = dry 8/23: B2022.033 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.13 in. (3 mm); aspect ratio = 6:5 sealant = dry 9/23: B2022.034 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry 10/23: B2022.035 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry 11/23: B2022.036 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry 12/23: B2022.037 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 13/23: B2022.038 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 14/23: B2022.039 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 15/23: B2022.040 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry 16/23: B2022.041 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry 17/23: B2022.051 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 18/23: B2022.052 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 19/23: B2022.053 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Seamed Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 20/23: B2022.054 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Polished Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 21/23: B2022.061 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1/4 in. (6 mm) HS monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 22/23: B2022.081 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN insulating glass unit (IGU) [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 23/23: B2022.082 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | (all): Glass cracking. | (all): Replace cracked glass panel. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | B2022\.0([023456]\w+¦8[12]) | Curtain Walls (2DS) | Non-structural | Enclosure | Glazing | Glass falls from frame. | 1/23: B2022.001 - Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 2/23: B2022.002 - Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Insulating Glass Units (dual pane), Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 3/23: B2022.021 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 4/23: B2022.022 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 5/23: B2022.023 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 6/23: B2022.031 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 7/23: B2022.032 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0 in. (0 mm); aspect ratio = 6:5 sealant = dry 8/23: B2022.033 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.13 in. (3 mm); aspect ratio = 6:5 sealant = dry 9/23: B2022.034 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry 10/23: B2022.035 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry 11/23: B2022.036 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry 12/23: B2022.037 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 13/23: B2022.038 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 14/23: B2022.039 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 15/23: B2022.040 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry 16/23: B2022.041 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry 17/23: B2022.051 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 18/23: B2022.052 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet 19/23: B2022.053 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Seamed Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 20/23: B2022.054 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Polished Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 21/23: B2022.061 - Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1/4 in. (6 mm) HS monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 22/23: B2022.081 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN insulating glass unit (IGU) [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry 23/23: B2022.082 - Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | (all): Glass falls from frame. | (all): Replace cracked glass panel; cover exposure in meantime. | 2 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 5 | 1 | 3 | 0 | rapid | 0
1 | B2023\.0[0124]\w+ | Storefronts (3 DS) | Non-structural | Enclosure | Glazing | Gasket seal failure. | 1/5: B2023.001 - Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 2/5: B2023.002 - Generic Storefront, Config: IGU, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 3/5: B2023.011 - Storefront, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry 4/5: B2023.021 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry 5/5: B2023.041 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU; glass-frame clearance = 0.59 in. (15 mm); aspect ratio = 6:5 sealant = dry | (all): Gasket seal failure. | (all): Remove glass panel and replace damaged gaskets. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | B2023\.0[0124]\w+ | Storefronts (3 DS) | Non-structural | Enclosure | Glazing | Glass cracking. | 1/5: B2023.001 - Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 2/5: B2023.002 - Generic Storefront, Config: IGU, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 3/5: B2023.011 - Storefront, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry 4/5: B2023.021 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry 5/5: B2023.041 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU; glass-frame clearance = 0.59 in. (15 mm); aspect ratio = 6:5 sealant = dry | (all): Glass cracking. | (all): Replace cracked glass panel. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | B2023\.0[0124]\w+ | Storefronts (3 DS) | Non-structural | Enclosure | Glazing | Glass falls out. | 1/5: B2023.001 - Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 2/5: B2023.002 - Generic Storefront, Config: IGU, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown 3/5: B2023.011 - Storefront, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry 4/5: B2023.021 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry 5/5: B2023.041 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU; glass-frame clearance = 0.59 in. (15 mm); aspect ratio = 6:5 sealant = dry | (all): Glass falls out. | (all): Replace cracked glass panel; cover exposure in meantime. | 3 | NA | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | component | 5 | 1 | 3 | 0 | rapid | 0
0 | B2023\.03[0-4] | Storefronts (2 DS, monolithic) | Non-structural | Enclosure | Glazing | Glass cracking. | 1/4: B2023.031 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Planar Specimen; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet 2/4: B2023.032 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, in-plane; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet 3/4: B2023.033 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, combined; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet 4/4: B2023.034 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, Short side; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 2.72:1 sealant = wet | (all): Glass cracking. | (all): Remove glass, replace frame, reinstall glass | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | B2023\.03[0-4] | Storefronts (2 DS, monolithic) | Non-structural | Enclosure | Glazing | Frame Damage | 1/4: B2023.031 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Planar Specimen; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet 2/4: B2023.032 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, in-plane; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet 3/4: B2023.033 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, combined; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet 4/4: B2023.034 - Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, Short side; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 2.72:1 sealant = wet | (all): Frame Damage | (all): Remove and replace frame and glass. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | B2023\.05[1-8] | Storefronts (2 DS, dual pane) | Non-structural | Enclosure | Glazing | Panel damage (no glass damage). | 1/8: B2023.051 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry 2/8: B2023.052 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry 3/8: B2023.053 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry 4/8: B2023.054 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.83:1 sealant = dry 5/8: B2023.055 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry 6/8: B2023.056 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry 7/8: B2023.057 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry 8/8: B2023.058 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.82:1 sealant = dry | (all): Panel damage (no glass damage). | (all): Remove glass, replace frame, replace panel. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | B2023\.05[1-8] | Storefronts (2 DS, dual pane) | Non-structural | Enclosure | Glazing | Glass cracks. | 1/8: B2023.051 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry 2/8: B2023.052 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry 3/8: B2023.053 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry 4/8: B2023.054 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.83:1 sealant = dry 5/8: B2023.055 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry 6/8: B2023.056 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry 7/8: B2023.057 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry 8/8: B2023.058 - Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.82:1 sealant = dry | (all): Glass cracks. | (all): Remove panel, replace glass, replace panel. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | B3011\.01[1234] | Roof tiles | Non-structural | Roof | Covering | Minor damage; tiles dislodged. | 1/4: B3011.011 - Concrete tile roof, tiles secured and compliant with UBC94 2/4: B3011.012 - Clay tile roof, tiles secured and compliant with UBC94 3/4: B3011.013 - Concrete tile roof, unsecured tiles 4/4: B3011.014 - Clay tile roof, unsecured tiles | (all): Minor damage; tiles dislodged. | ~~~ 1,3 ~~~ Reinstall dislodged tiles. ~~~ 2,4 ~~~ Replace and install dislodged tiles (assume 5% of area) | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | B3011\.01[1234] | Roof tiles | Non-structural | Roof | Covering | Major portion of tile dislodged. | 1/4: B3011.011 - Concrete tile roof, tiles secured and compliant with UBC94 2/4: B3011.012 - Clay tile roof, tiles secured and compliant with UBC94 3/4: B3011.013 - Concrete tile roof, unsecured tiles 4/4: B3011.014 - Clay tile roof, unsecured tiles | (all): Major portion of tile dislodged. | ~~~ 1,3 ~~~ Reinstall dislodged tiles. ~~~ 2,4 ~~~ Replace and install dislodged tiles. | 2 | NA | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | component | 5 | 1 | 7 | 0 | rapid | 0
1 | B3031\.00[12][a-c] | Masonry chimney (unreinforced, non industrial) | Non-structural | Roof | Chimney | Cracking with offset > 1/16" | 1/6: B3031.001a - Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with masonry 2/6: B3031.001b - Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with masonry 3/6: B3031.001c - Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with masonry 4/6: B3031.002a - Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with framing 5/6: B3031.002b - Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with framing 6/6: B3031.002c - Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with framing | (all): Cracking with offset > 1/16" | (all): Rebuild above break or replace entire chimney. Addl comments (edit or delete as necessary): Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | B3031\.00[12][a-c] | Masonry chimney (unreinforced, non industrial) | Non-structural | Roof | Chimney | Toppling of all or a portion of the chimney. | 1/6: B3031.001a - Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with masonry 2/6: B3031.001b - Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with masonry 3/6: B3031.001c - Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with masonry 4/6: B3031.002a - Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with framing 5/6: B3031.002b - Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with framing 6/6: B3031.002c - Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with framing | (all): Toppling of all or a portion of the chimney. | (all): Rebuild above break or replace entire chimney. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | B3041\.001 | URM Parapet | Non-structural | Roof | Parapet | Cracking with offset > 1/16" | 1/1: B3041.001 - Masonry Parapet - unreinforced, unbraced | (all): Cracking with offset > 1/16" | (all): Replace and reinforce | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 1 | 7 | 0 | rapid | 0
0 | B3041\.001 | URM Parapet | Non-structural | Roof | Parapet | Toppling of all or portion of parapet. | 1/1: B3041.001 - Masonry Parapet - unreinforced, unbraced | (all): Toppling of all or portion of parapet. | (all): Replace and reinforce | 2 | NA | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | component | 5 | 1 | 7 | 0 | full | 1
1 | C1011\.[23]\w+ | Partition Wall and Wall Finishes (wood studs) | Non-structural | Interior | Partition Walls | minor aesthetic damage (cracking of paint, etc.) | 1/4: C1011.211a - Wall Partition - Type: Gypsum with wood studs (both sides), Full Height, Fixed Below, Fixed Above 2/4: C1011.311a - Interior of Exterior Wall - Type: Gypsum with wood studs (single-sided gypsum), Full Height, Fixed Below, Fixed Above 3/4: C1011.222a - Wall Partition - Type: Plaster on wood lath with wood studs (both sides), Full Height, Fixed Below, Fixed Above 4/4: C1011.322a - Interior of Exterior Wall -Type: Plaster on wood lath with wood studs (single-sided plaster), Full Height, Fixed Below, Fixed Above | ~~~ 1-2 ~~~ Cracking of paint over fasteners or joints. ~~~ 3-4 ~~~ Cracking of plaster at corners and openings. Slightly spalled sections of plaster near openings and thin (< 1/8") cracks extending across solid panel sections. | ~~~ 1-2 ~~~ Gypsum wallboard repaired by replacing the tape along the seam of two adjacent panels and local areas with popped fasteners, applying new joint compound, sanding, and repainting. ~~~ 3-4 ~~~ Lath and plaster repaired by cleaning cracked areas, applying new plaster, sanding, and repainting. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | C1011\.[23]\w+ | Partition Wall and Wall Finishes (wood studs) | Non-structural | Interior | Partition Walls | damage to wallboard, not studs | 1/4: C1011.211a - Wall Partition - Type: Gypsum with wood studs (both sides), Full Height, Fixed Below, Fixed Above 2/4: C1011.311a - Interior of Exterior Wall - Type: Gypsum with wood studs (single-sided gypsum), Full Height, Fixed Below, Fixed Above 3/4: C1011.222a - Wall Partition - Type: Plaster on wood lath with wood studs (both sides), Full Height, Fixed Below, Fixed Above 4/4: C1011.322a - Interior of Exterior Wall -Type: Plaster on wood lath with wood studs (single-sided plaster), Full Height, Fixed Below, Fixed Above | ~~~ 1-2 ~~~ Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. ~~~ 3-4 ~~~ Significant cracking and spalling of plaster at corners and openings. Widespread minor cracking in continuous sections of plaster. Local removal and repairs are still economical. | ~~~ 1-2 ~~~ Replace 25 feet of the affected panel along with the application of new tape, joint compound, followed by sanding and repainting. Studs are not damaged. ~~~ 3-4 ~~~ Cut back damaged (spalled) plaster areas and tie in new plaster to existing finish, followed by sanding and repainting. Studs are not damaged. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | C1011\.[23]\w+ | Partition Wall and Wall Finishes (wood studs) | Non-structural | Interior | Partition Walls | damage to studs | 1/4: C1011.211a - Wall Partition - Type: Gypsum with wood studs (both sides), Full Height, Fixed Below, Fixed Above 2/4: C1011.311a - Interior of Exterior Wall - Type: Gypsum with wood studs (single-sided gypsum), Full Height, Fixed Below, Fixed Above 3/4: C1011.222a - Wall Partition - Type: Plaster on wood lath with wood studs (both sides), Full Height, Fixed Below, Fixed Above 4/4: C1011.322a - Interior of Exterior Wall -Type: Plaster on wood lath with wood studs (single-sided plaster), Full Height, Fixed Below, Fixed Above | ~~~ 1-2 ~~~ Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard, but framing adjustments possible for this damage state. ~~~ 3-4 ~~~ Widespread damage of plaster finish including bulging out-of-plane and delamination. | ~~~ 1-2 ~~~ Replace 100 feet of the affected panel along with the application of new tape, joint compound, followed by sanding and repainting. Studs are not damaged. ~~~ 3-4 ~~~ Removal of plaster and wood lath, furring of framing to match previous finish thickness when applying gypsum wallboard, followed by sanding and repainting. Studs are not typcially not damaged but may need local repairs or adjustment. | 3 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 11 | 1 | 7 | 0 | rapid | 0
0 | C1011\.001[abc] | Partition Wall and Wall Finishes (metal studs) | Non-structural | Interior | Partition Walls | Screw pop-out, cracking of wall board, warping or cracking of tape, slight crushing of wall panel at corners. | 1/3: C1011.001a - Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Fixed Above 2/3: C1011.001b - Wall Partition, Type: Gypsum with metal studs, Partial Height, Fixed Below, Lateral Braced Above 3/3: C1011.001c - Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above with returns | (all): Screw pop-out, cracking of wall board, warping or cracking of tape, slight crushing of wall panel at corners. | (all): Retape joints, paste and repaint. May require cutting and replacing corner sections of board. Repair 5% wallboard, 10% retape, 25% repaint. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
0 | C1011\.001[abc] | Partition Wall and Wall Finishes (metal studs) | Non-structural | Interior | Partition Walls | Moderate cracking or crushing of gypsum wall boards (typically in corners). Moderate corner gap openings, bending of boundary studs. | 1/3: C1011.001a - Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Fixed Above 2/3: C1011.001b - Wall Partition, Type: Gypsum with metal studs, Partial Height, Fixed Below, Lateral Braced Above 3/3: C1011.001c - Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above with returns | (all): Moderate cracking or crushing of gypsum wall boards (typically in corners). Moderate corner gap openings, bending of boundary studs. | (all): Remove and replace 10% of wall board (both sides), retape and paste 25% of wall, paint 50% of wall. Replace boundary studs of approximately 5 intersections per 100 ft of wall length. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | C1011\.001[abc] | Partition Wall and Wall Finishes (metal studs) | Non-structural | Interior | Partition Walls | Buckling of studs and tearing of tracks. Tearing or bending of top track, tearing at corners with transverse walls, large gap openings, walls displaced. | 1/3: C1011.001a - Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Fixed Above 2/3: C1011.001b - Wall Partition, Type: Gypsum with metal studs, Partial Height, Fixed Below, Lateral Braced Above 3/3: C1011.001c - Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above with returns | (all): Buckling of studs and tearing of tracks. Tearing or bending of top track, tearing at corners with transverse walls, large gap openings, walls displaced. | (all): Remove and replace 50% of length of metal stud wall, 50% of both sides of the gypsum, and any embedded utilities. Retape and paste as required. Repaint 100%. | 3 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 11 | 1 | 7 | 0 | rapid | 0
1 | C1011\.001d | Slip Track w/o returns | Non-structural | Interior | Partition Walls | Screw pop-out, cracking of wall board, warping or cracking of tape, slight crushing of wall panel at corners. | 1/1: C1011.001d - Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above w/o returns (friction connections) | (all): Screw pop-out, cracking of wall board, warping or cracking of tape, slight crushing of wall panel at corners. | (all): Retape joints, paste and repaint. May require cutting and replacing corner sections of board. Repair 5% wallboard, 10% retape, 25% repaint. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | C1011\.001d | Slip Track w/o returns | Non-structural | Interior | Partition Walls | Moderate cracking or crushing of gypsum wall boards (typically in corners). Moderate corner gap openings, bending of boundary studs. | 1/1: C1011.001d - Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above w/o returns (friction connections) | (all): Moderate cracking or crushing of gypsum wall boards (typically in corners). Moderate corner gap openings, bending of boundary studs. | (all): Remove and replace 10% of wall board (both sides), retape and paste 25% of wall, paint 50% of wall. Replace boundary studs of approximately 5 intersections per 100 ft of wall length. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | C1011\.011a | Full Fixed | Non-structural | Interior | Partition Walls | Cracking of paint over fasteners or joints. | 1/1: C1011.011a - Wall Partition, Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | (all): Cracking of paint over fasteners or joints. | (all): Gypsum wallboard repaired by replacing the tape along the seam of two adjacent panels, applying new joint compound, sanding, and repainting. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
0 | C1011\.011a | Full Fixed | Non-structural | Interior | Partition Walls | Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. | 1/1: C1011.011a - Wall Partition, Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | (all): Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. | (all): Replace 25 feet of the affected panel along with the application of new tape, joint compound, followed by sanding and repainting. Studs are not damaged. | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 5 | 1 | 7 | 0 | rapid | 0
0 | C1011\.011a | Full Fixed | Non-structural | Interior | Partition Walls | Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. | 1/1: C1011.011a - Wall Partition, Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | (all): Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. | (all): Replace 100 feet of the affected panel along with the application of new tape, joint compound, followed by sanding and repainting. Studs are not damaged. | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 11 | 1 | 7 | 0 | rapid | 0
1 | C2011\.\w+ | Stairs | Non-structural | Stairs | Stairs | Aesthetic damage | 1/11: C2011.001a - Prefabricated steel stair with steel treads and landings with seismic joints that accommodate drift. 2/11: C2011.001b - Prefabricated steel stair with steel treads and landings with no seismic joint. 3/11: C2011.011a - Non-monolithic precast concrete stair assembly with concrete stringers and treads with seismic joints that accommodate drift. 4/11: C2011.011b - Non-monolithic precast concrete stair assembly with concrete stringers and treads with no seismic joint. 5/11: C2011.021a - Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace in kind if replacement is required. 6/11: C2011.021b - Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace in kind if replacement is required. 7/11: C2011.021c - Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace with prefabricated steel stair if replacement is required. 8/11: C2011.021d - Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace with prefabricated steel stair if replacement is required. 9/11: C2011.031a - Hybrid stair assembly with steel stringers and concrete treads and landings with seismic joints that accommodate drift. 10/11: C2011.031b - Hybrid stair assembly with steel stringers and concrete treads and landings with no seismic joints. 11/11: C2011.041b - Light frame stair fragility. Approximation as a placeholder until there is more research on the topic. Damage states from P-58 Light frame stair example. Costing approximated from various online sources for stair replacement. | ~~~ 1-2 ~~~ Non structural damage, local steel yielding. ~~~ 3-4 ~~~ Non structural damage, local concrete cracking, localized concrete spalling, localized rebar yielding. ~~~ 5-8 ~~~ Local concrete cracking, localized concrete spalling ~~~ 9-10 ~~~ Localized steel yielding. ~~~ 11 ~~~ Cosmetic Damage. | ~~~ 1-2 ~~~ Patch, paint. ~~~ 3-4 ~~~ Patch, paint, epoxy injection. Repair finishes. ~~~ 5-8 ~~~ Protect surrounding space, epoxy inject cracks, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. ~~~ 9-10 ~~~ Protect surrounding space. Minor repair of finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. ~~~ 11 ~~~ Repair cosmetic damage. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | C2011\.\w+ | Stairs | Non-structural | Stairs | Stairs | Structural damage, but live load capacity remains intact | 1/11: C2011.001a - Prefabricated steel stair with steel treads and landings with seismic joints that accommodate drift. 2/11: C2011.001b - Prefabricated steel stair with steel treads and landings with no seismic joint. 3/11: C2011.011a - Non-monolithic precast concrete stair assembly with concrete stringers and treads with seismic joints that accommodate drift. 4/11: C2011.011b - Non-monolithic precast concrete stair assembly with concrete stringers and treads with no seismic joint. 5/11: C2011.021a - Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace in kind if replacement is required. 6/11: C2011.021b - Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace in kind if replacement is required. 7/11: C2011.021c - Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace with prefabricated steel stair if replacement is required. 8/11: C2011.021d - Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace with prefabricated steel stair if replacement is required. 9/11: C2011.031a - Hybrid stair assembly with steel stringers and concrete treads and landings with seismic joints that accommodate drift. 10/11: C2011.031b - Hybrid stair assembly with steel stringers and concrete treads and landings with no seismic joints. 11/11: C2011.041b - Light frame stair fragility. Approximation as a placeholder until there is more research on the topic. Damage states from P-58 Light frame stair example. Costing approximated from various online sources for stair replacement. | ~~~ 1 ~~~ Structural damage but live load capacity remains intact. Buckling of steel, weld cracking. ~~~ 2,9-10 ~~~ Buckling of steel, weld cracking. ~~~ 3-4 ~~~ Structural damage but live load capacity remains intact. Extensive concrete cracking, concrete crushing, buckling of rebar. ~~~ 5-8 ~~~ Extensive concrete cracking, concrete crushing ~~~ 11 ~~~ Structural damage but live load capacity remains intact. | ~~~ 1-2 ~~~ Removal and replacement of damaged components. Field repair of damage (such as welding). Repair finsihes. ~~~ 3-4 ~~~ Remove damaged components, install replacement components. ~~~ 5-8 ~~~ Protect floor, cut out damaged areas, repair buckled rebar, patch / cast concrete, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. ~~~ 9-10 ~~~ Protect floor, cut out damaged areas, reweld. Repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. ~~~ 11 ~~~ Repair damage. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | full | 1
1 | C2011\.\w+ | Stairs | Non-structural | Stairs | Stairs | Loss of live load capacity | 1/11: C2011.001a - Prefabricated steel stair with steel treads and landings with seismic joints that accommodate drift. 2/11: C2011.001b - Prefabricated steel stair with steel treads and landings with no seismic joint. 3/11: C2011.011a - Non-monolithic precast concrete stair assembly with concrete stringers and treads with seismic joints that accommodate drift. 4/11: C2011.011b - Non-monolithic precast concrete stair assembly with concrete stringers and treads with no seismic joint. 5/11: C2011.021a - Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace in kind if replacement is required. 6/11: C2011.021b - Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace in kind if replacement is required. 7/11: C2011.021c - Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace with prefabricated steel stair if replacement is required. 8/11: C2011.021d - Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace with prefabricated steel stair if replacement is required. 9/11: C2011.031a - Hybrid stair assembly with steel stringers and concrete treads and landings with seismic joints that accommodate drift. 10/11: C2011.031b - Hybrid stair assembly with steel stringers and concrete treads and landings with no seismic joints. 11/11: C2011.041b - Light frame stair fragility. Approximation as a placeholder until there is more research on the topic. Damage states from P-58 Light frame stair example. Costing approximated from various online sources for stair replacement. | ~~~ 1-2 ~~~ Loss of live load capacity. Connection and or weld fracture. ~~~ 3-4 ~~~ Loss of live load capacity. Extensive concrete crushing, connection failure. ~~~ 5-11 ~~~ Loss of live load capacity. | ~~~ 1-4 ~~~ Replace stair and handrail. Repair and replace affected soffits and floor finishes. ~~~ 5-10 ~~~ Protect area, remove damaged stair including landings and handrails. Remove and reinstall damaged soffit and mechanical systems. Replace stair, landings, and handrail. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. ~~~ 11 ~~~ Replace stair. | 3 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | NA | 4 | 0 | 0 | 0 | full | 1
0 | C3011\.00[23][abcd] | Tile and Marble Finish | Non-structural | Interior | Partition Walls | Minor aesthetic damage | 1/8: C3011.002a - Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Fixed Above 2/8: C3011.002b - Wall Partition, Type: Gypsum + Ceramic Tile, Partial Height, Fixed Below, Lateral Braced Above 3/8: C3011.002c - Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) 4/8: C3011.002d - Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) 5/8: C3011.003a - Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Fixed Above 6/8: C3011.003b - Wall Partition, Type: High End Marble or Wood Panel, Partial Height, Fixed Below, Lateral Braced Above 7/8: C3011.003c - Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) 8/8: C3011.003d - Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | ~~~ 1-4 ~~~ Minor cracked joints and tile. ~~~ 5-8 ~~~ minor cracked joints and minor cracks in marble / wood paneling. | ~~~ 1-4 ~~~ Carefully remove cracked tile and grout at cracked joints, install new ceramic tile and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain in place. ~~~ 5-8 ~~~ Carefully remove cracked marble/paneling and grout at cracked joints, and install new marble/paneling and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain place. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | C3011\.00[23][abcd] | Tile and Marble Finish | Non-structural | Interior | Partition Walls | Major aesthetic damage | 1/8: C3011.002a - Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Fixed Above 2/8: C3011.002b - Wall Partition, Type: Gypsum + Ceramic Tile, Partial Height, Fixed Below, Lateral Braced Above 3/8: C3011.002c - Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) 4/8: C3011.002d - Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) 5/8: C3011.003a - Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Fixed Above 6/8: C3011.003b - Wall Partition, Type: High End Marble or Wood Panel, Partial Height, Fixed Below, Lateral Braced Above 7/8: C3011.003c - Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) 8/8: C3011.003d - Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | ~~~ 1-4 ~~~ Cracked joints and tile. ~~~ 5-8 ~~~ significant cracks in marble / wood paneling. | ~~~ 1-4 ~~~ Install ceramic tile and grout all joints for full 100 foot length of wall. Note: gypsum wall board will also be removed and replaced which means the removal of ceramic tile will be part of the gypsum wall board removal. ~~~ 5-8 ~~~ Install new marble/paneling for full 100 foot length of wall. Note: the gypsum wall board will also be removed and replaced which means the removal of the marble/paneling will be part of the gypsum wall board removal. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 3 | 1 | 3 | 0 | rapid | 0
1 | C3011\.001[a-d] | Wall Partition, Type: Gypsum + Wallpaper | Non-structural | Interior | Partition Walls | Wall paper warped and torn. | 1/4: C3011.001a - Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Fixed Above 2/4: C3011.001b - Wall Partition, Type: Gypsum + Wallpaper, Partial Height, Fixed Below, Lateral Braced Above 3/4: C3011.001c - Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) 4/4: C3011.001d - Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | (all): Wall paper warped and torn. | (all): Remove existing wall paper (or wall) and install new wall paper for full 100 foot length of wall. Existing wall damage per wall type NISTIR file. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | C3021\.\w+ | Generic Floor Covering | Non-structural | Interior | Floors | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. | 1/16: C3021.001a - Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Dry 2/16: C3021.001b - Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Humid 3/16: C3021.001c - Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Dry 4/16: C3021.001d - Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Humid 5/16: C3021.001e - Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Dry 6/16: C3021.001f - Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Humid 7/16: C3021.001g - Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Dry 8/16: C3021.001h - Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Humid 9/16: C3021.001i - Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Dry 10/16: C3021.001j - Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Humid 11/16: C3021.001k - Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Dry 12/16: C3021.001l - Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Humid 13/16: C3021.001m - Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Dry 14/16: C3021.001n - Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Humid 15/16: C3021.001o - Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Dry 16/16: C3021.001p - Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Humid | (all): Flooding of all or a portion of the total floor associated with a major leakage of a pipe. | (all): Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | C3027\.\w+ | Access Pedastal Flooring | Non-structural | Interior | Floors | Minor damage to the flooring system. Damage to the equipment of the flooring system. | 1/2: C3027.001 - Raised Access Floor, non seismically rated. 2/2: C3027.002 - Raised Access Floor, seismically rated. | (all): Minor damage to the flooring system. Damage to the equipment of the flooring system. | (all): Repair the flooring system, assume cost equal to 5% of the replacement cost. Repair the flooring equipment, assume a cost equal to 10% of the replacement cost. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | C3032\.00[134][a-d] | Suspended Ceiling | Non-structural | Interior | Ceilings | 5 % of ceiling grid and tile damage. | 1/12: C3032.001a - Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only 2/12: C3032.001b - Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only 3/12: C3032.001c - Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only 4/12: C3032.001d - Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only 5/12: C3032.003a - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A < 250, Vert & Lat support 6/12: C3032.003b - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 250 < A < 1000, Vert & Lat support 7/12: C3032.003c - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 1000 < A < 2500, Vert & Lat support 8/12: C3032.003d - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A > 2500, Vert & Lat support 9/12: C3032.004a - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A < 250, Vert & Lat support 10/12: C3032.004b - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 250 < A < 1000, Vert & Lat support 11/12: C3032.004c - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 1000 < A < 2500, Vert & Lat support 12/12: C3032.004d - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A > 2500, Vert & Lat support | (all): 5 % of ceiling grid and tile damage. | (all): Reinstall, repair, or replace 5% of the ceiling area. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | component | 1 | 0 | 0 | 0 | rapid | 0
0 | C3032\.00[134][a-d] | Suspended Ceiling | Non-structural | Interior | Ceilings | 30% of ceiling grid and tile damage. | 1/12: C3032.001a - Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only 2/12: C3032.001b - Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only 3/12: C3032.001c - Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only 4/12: C3032.001d - Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only 5/12: C3032.003a - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A < 250, Vert & Lat support 6/12: C3032.003b - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 250 < A < 1000, Vert & Lat support 7/12: C3032.003c - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 1000 < A < 2500, Vert & Lat support 8/12: C3032.003d - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A > 2500, Vert & Lat support 9/12: C3032.004a - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A < 250, Vert & Lat support 10/12: C3032.004b - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 250 < A < 1000, Vert & Lat support 11/12: C3032.004c - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 1000 < A < 2500, Vert & Lat support 12/12: C3032.004d - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A > 2500, Vert & Lat support | (all): 30% of ceiling grid and tile damage. | (all): Replace 30% of the ceiling area. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.3 | component | 3 | 1 | 3 | 0 | rapid | 0
0 | C3032\.00[134][a-d] | Suspended Ceiling | Non-structural | Interior | Ceilings | 50% of ceiling grid and tile damage. | 1/12: C3032.001a - Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only 2/12: C3032.001b - Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only 3/12: C3032.001c - Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only 4/12: C3032.001d - Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only 5/12: C3032.003a - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A < 250, Vert & Lat support 6/12: C3032.003b - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 250 < A < 1000, Vert & Lat support 7/12: C3032.003c - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 1000 < A < 2500, Vert & Lat support 8/12: C3032.003d - Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A > 2500, Vert & Lat support 9/12: C3032.004a - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A < 250, Vert & Lat support 10/12: C3032.004b - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 250 < A < 1000, Vert & Lat support 11/12: C3032.004c - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 1000 < A < 2500, Vert & Lat support 12/12: C3032.004d - Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A > 2500, Vert & Lat support | (all): 50% of ceiling grid and tile damage. | (all): Replace the entire ceiling | 3 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0.5 | component | 7 | 1 | 7 | 0 | rapid | 0
1 | C3034\.\w+ | Independent Pendant Lighting | Non-structural | Interior | Lighting | Disassembly of rod system at connections with horizontal light fixture, low cycle fatigue failure of the threaded rod, pullout of rods from ceiling assembly. | 1/2: C3034.001 - Independent Pendant Lighting - non seismic 2/2: C3034.002 - Independent Pendant Lighting - seismically rated | (all): Disassembly of rod system at connections with horizontal light fixture, low cycle fatigue failure of the threaded rod, pullout of rods from ceiling assembly. | (all): Replace damaged lighting components. | 1 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 100 | component | 3 | 1 | 7 | 0 | rapid | 0
0 | D1014\.0[34]1 | Traction Elevators (HBRG): Machine Room | Non-structural | Conveying | Elevators | Controller anchorage failure, machine anchorage failure, motor Generator anchorage failure, governor anchorage failure, and rope guard/tail sheave anchorage failure. | 1/2: D1014.031 - Traction Elevator Machine room components. Applies to Seismic Zone 2 and elevators designed according to the ASME A17.1-2007 Standard or similar. 2/2: D1014.041 - Traction Elevator Machine room component anchorage. Applies to Seismic Zone 3 or greater and elevators designed according to the ASME A17.1-2007 Standard or similar. | (all): Controller anchorage failure, machine anchorage failure, motor Generator anchorage failure, governor anchorage failure, and rope guard/tail sheave anchorage failure. | (all): Reinstall or replace controller. Reinstall or replace motor generator and or Install new generator with appropriate anchors. Install new governor. Reinstall or replace rope guards and or repair or replace tail sheave. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | D1014\.0[34]2 | Traction Elevators (HBRG): Cab and Counterweights | Non-structural | Conveying | Elevators | Car guide shoes damaged, counterweight guide shoes damaged, counterweight distorted frame, cab ceiling damaged, cab stabilizer brackets bent, and or cab walls, and or cab doors damaged. | 1/2: D1014.032 - Traction Elevator Cab and Counterweight Components. Applies to Seismic Zone 2 and elevators designed according to the ASME A17.1-2007 Standard or similar. 2/2: D1014.042 - Traction Elevator Cab and Counterweight Components. Applies to Seismic Zone 3 or greater and elevators designed according to the ASME A17.1-2007 Standard or similar. | (all): Car guide shoes damaged, counterweight guide shoes damaged, counterweight distorted frame, cab ceiling damaged, cab stabilizer brackets bent, and or cab walls, and or cab doors damaged. | (all): Repalce car guide shoes. Replace counterweight guide shoe. Repair or replace counterweight frame. Repair or replace cab ceiling. Repair or replace cab walls. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
0 | D1014\.0[34]3 | Traction Elevators (HBRG): Guide Rails | Non-structural | Conveying | Elevators | Guide rail distortion | 1/2: D1014.033 - Traction Elevator Guide Rails. Applies to Seismic Zone 2 and elevators designed according to the ASME A17.1-2007 Standard or similar. 2/2: D1014.043 - Traction Elevator Guide Rails. Applies to Seismic Zone 3 or greater and elevators designed according to the ASME A17.1-2007 Standard or similar. | (all): Guide rail distortion | (all): Replace rail. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | D1014\.0[34]4 | Traction Elevators (HBRG): Rail Brackets | Non-structural | Conveying | Elevators | Intermediate guide rail brackets break or bend, car guide rail brackets break or bend, and counterweight guide rail brackets break or bend. | 1/2: D1014.034 - Traction Elevator Guide Rail Brackets. Applies to Seismic Zone 2 and elevators designed according to the ASME A17.1-2007 Standard or similar. 2/2: D1014.044 - Traction Elevator Guide Rail Brackets. Applies to Seismic Zone 3 or greater and elevators designed according to the ASME A17.1-2007 Standard or similar. | (all): Intermediate guide rail brackets break or bend, car guide rail brackets break or bend, and counterweight guide rail brackets break or bend. | (all): Replace intermediate brackets. Replace brackets r tie rod. Replace counterweight brackets. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
0 | D1014\.01\w+ | Traction Elevators | Non-structural | Conveying | Elevators | Controller anchorage failed, and or machine anchorage failed, and or motor generator anchorage failed, and or governor anchorage failed, and or rope guard failures. | 1/2: D1014.011 - Traction Elevator - Applies to most California Installations 1976 or later, most western states installations 1982 or later and most other U.S installations 1998 or later. 2/2: D1014.012 - Traction Elevator - Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most other U.S installations prior to 1998. | (all): Controller anchorage failed, and or machine anchorage failed, and or motor generator anchorage failed, and or governor anchorage failed, and or rope guard failures. | (all): Multiple repairs possible (% change of each): Reinstall or replace controller (4%), and or reinstall or replace motor generator (63%), and or Install new generator with appropriate anchors (23%), and or Install new governor (7%), and or Reinstall or replace rope guards (15%). | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
0 | D1014\.01\w+ | Traction Elevators | Non-structural | Conveying | Elevators | Rail distortion, and or intermediate bracket separate and spread, and or counterweight bracket break or bend, and or car bracket break or bend, and or car guide shoes damaged, and or counterweight guide shoes damaged, and or counterweight frame distortion, and or tail sheave dislodged and/or twisted | 1/2: D1014.011 - Traction Elevator - Applies to most California Installations 1976 or later, most western states installations 1982 or later and most other U.S installations 1998 or later. 2/2: D1014.012 - Traction Elevator - Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most other U.S installations prior to 1998. | (all): Rail distortion, and or intermediate bracket separate and spread, and or counterweight bracket break or bend, and or car bracket break or bend, and or car guide shoes damaged, and or counterweight guide shoes damaged, and or counterweight frame distortion, and or tail sheave dislodged and/or twisted | (all): Multiple repairs possible (% change of each): Replace rail (62%), and or replace bracket or tie rod (28%), and or replace counterweight bracket 14%), and or replace intermediate bracket (28%), and or replace car guide shoes (35%), and or replace counterweight guide shoe (28%), and or repair or replace counterweight frame (28%), and or repair or replace tail sheave (1%) | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
0 | D1014\.01\w+ | Traction Elevators | Non-structural | Conveying | Elevators | Cab stabilizers bent, or cab walls damaged, or cab doors damaged. | 1/2: D1014.011 - Traction Elevator - Applies to most California Installations 1976 or later, most western states installations 1982 or later and most other U.S installations 1998 or later. 2/2: D1014.012 - Traction Elevator - Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most other U.S installations prior to 1998. | (all): Cab stabilizers bent, or cab walls damaged, or cab doors damaged. | (all): Multiple repairs possible (% change of each): Repair or replace cab walls (3%), and or repair or replace cab doors (17%), and or repair or replace cab stabilizers (92%) | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
0 | D1014\.01\w+ | Traction Elevators | Non-structural | Conveying | Elevators | Cab ceiling damaged. | 1/2: D1014.011 - Traction Elevator - Applies to most California Installations 1976 or later, most western states installations 1982 or later and most other U.S installations 1998 or later. 2/2: D1014.012 - Traction Elevator - Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most other U.S installations prior to 1998. | (all): Cab ceiling damaged. | (all): Multiple repairs possible (% change of each): Repair or replace cab ceiling (100%) | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | D1014\.02\w+ | Hydraulic Elevators | Non-structural | Conveying | Elevators | Damaged controls. | 1/2: D1014.021 - Hydraulic Elevator - Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. 2/2: D1014.022 - Hydraulic Elevator - Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most U.S installations prior to 1998. | (all): Damaged controls. | (all): Multiple repairs possible (% change of each): Repair damaged controls (100%) | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | D1014\.02\w+ | Hydraulic Elevators | Non-structural | Conveying | Elevators | Damaged vane and hoist-way switches, and or bent cab stabilizers, and or damaged car guide shoes. | 1/2: D1014.021 - Hydraulic Elevator - Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. 2/2: D1014.022 - Hydraulic Elevator - Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most U.S installations prior to 1998. | (all): Damaged vane and hoist-way switches, and or bent cab stabilizers, and or damaged car guide shoes. | (all): Multiple repairs possible (% change of each): Repair damaged vane and hoist-way switches (41%), and or repair bent cab stabilizers (41%), and or repair damaged car guide shoes (41%). | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | D1014\.02\w+ | Hydraulic Elevators | Non-structural | Conveying | Elevators | Damaged entrance and car door, and or flooring damage. | 1/2: D1014.021 - Hydraulic Elevator - Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. 2/2: D1014.022 - Hydraulic Elevator - Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most U.S installations prior to 1998. | (all): Damaged entrance and car door, and or flooring damage. | ~~~ 1 ~~~ Multiple repairs possible (% change of each): Repair damage to doors (68%), and or repair flooring (46%) ~~~ 2 ~~~ Multiple repairs possible (% change of each): Repair damage to cab door (68%), and or repair cab flooring (46%) | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
1 | D1014\.02\w+ | Hydraulic Elevators | Non-structural | Conveying | Elevators | Oil leak in hydraulic line, and or hydraulic tank failure. | 1/2: D1014.021 - Hydraulic Elevator - Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. 2/2: D1014.022 - Hydraulic Elevator - Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most U.S installations prior to 1998. | (all): Oil leak in hydraulic line, and or hydraulic tank failure. | (all): Multiple repairs possible (% change of each): Repair oil leak in hydraulic line (27%), and or hydraulic tank failure (81%) | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 2 | 0 | 0 | 0 | rapid | 0
0 | D2021\.01[12]b | Cold Domestic Piping - Small diameter (brace only), SDC A-C | Non-structural | Piping | Domestic | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | 1/2: D2021.011b - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY 2/2: D2021.012b - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | (all): Lateral Brace Failure - 1 failure per 1000 feet of pipe. | (all): Replace failed lateral braces. One repair per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2021\.01[12]b | Cold Domestic Piping - Small diameter (brace only), SDC A-C | Non-structural | Piping | Domestic | Vertical Brace Failure - 1 failure per 1000 feet of pipe | 1/2: D2021.011b - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY 2/2: D2021.012b - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | (all): Vertical Brace Failure - 1 failure per 1000 feet of pipe | (all): Replace failed vertical braces. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2021\.01[1234]a | Cold Domestic Piping - Small diameter (branches) | Non-structural | Piping | Domestic | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | 1/4: D2021.011a - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY 2/4: D2021.012a - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY 3/4: D2021.013a - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY 4/4: D2021.014a - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | (all): Retighten flange bolts at leaking joints. One joint per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2021\.01[1234]a | Cold Domestic Piping - Small diameter (branches) | Non-structural | Piping | Domestic | Pipe Break - 1 break per 1000 feet of pipe. | 1/4: D2021.011a - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY 2/4: D2021.012a - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY 3/4: D2021.013a - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY 4/4: D2021.014a - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Pipe Break - 1 break per 1000 feet of pipe. | (all): Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | component | 5 | 0 | 0 | 0 | rapid | 0
0 | D2021\.01[34]b | Cold Domestic Piping - Small diameter (brace only), SDC D+ | Non-structural | Piping | Domestic | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | 1/2: D2021.013b - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY 2/2: D2021.014b - Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Lateral Brace Failure - 1 failure per 1000 feet of pipe. | (all): Replace failed lateral braces. One repair per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2021\.02[1234]a | Cold Domestic Piping - Large diameter (mains) | Non-structural | Piping | Domestic | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | 1/4: D2021.021a - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC A or B, PIPING FRAGILITY 2/4: D2021.022a - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC C, PIPING FRAGILITY 3/4: D2021.023a - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, PIPING FRAGILITY 4/4: D2021.024a - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), PIPING FRAGILITY | (all): Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | (all): Retighten flange bolts at leaking joints. One joint per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2021\.02[1234]a | Cold Domestic Piping - Large diameter (mains) | Non-structural | Piping | Domestic | Pipe Break - 1 break per 1000 feet of pipe. | 1/4: D2021.021a - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC A or B, PIPING FRAGILITY 2/4: D2021.022a - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC C, PIPING FRAGILITY 3/4: D2021.023a - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, PIPING FRAGILITY 4/4: D2021.024a - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), PIPING FRAGILITY | (all): Pipe Break - 1 break per 1000 feet of pipe. | (all): Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | component | 5 | 0 | 0 | 0 | rapid | 0
0 | D2021\.02[34]b | Cold Domestic Piping - Large diameter (brace only), SDC D+ | Non-structural | Piping | Domestic | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | 1/2: D2021.023b - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, BRACING FRAGILITY 2/2: D2021.024b - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), BRACING FRAGILITY | (all): Lateral Brace Failure - 1 failure per 1000 feet of pipe. | (all): Replace failed lateral braces. One repair per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2021\.02[34]b | Cold Domestic Piping - Large diameter (brace only), SDC D+ | Non-structural | Piping | Domestic | Vertical Brace Failure - 1 failure per 1000 feet of pipe | 1/2: D2021.023b - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, BRACING FRAGILITY 2/2: D2021.024b - Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), BRACING FRAGILITY | (all): Vertical Brace Failure - 1 failure per 1000 feet of pipe | (all): Replace failed vertical braces. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2022\.01[12]b | Hot Domestic Piping - Small diameter (bracing), SDC A-C | Non-structural | Piping | Domestic | Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2022.011b - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY 2/2: D2022.012b - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | (all): Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | (all): Replace failed supports. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2022\.01[12]b | Hot Domestic Piping - Small diameter (bracing), SDC A-C | Non-structural | Piping | Domestic | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2022.011b - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY 2/2: D2022.012b - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | (all): Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). | (all): Replace failed 60 ft pipe sections including supports. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2022\.01[1234]a | Hot Domestic Piping - Small diameter (branches) | Non-structural | Piping | Domestic | Small Leakage at joints - 1 leak per 1000 feet of pipe. | 1/4: D2022.011a - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY 2/4: D2022.012a - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY 3/4: D2022.013a - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY 4/4: D2022.014a - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Small Leakage at joints - 1 leak per 1000 feet of pipe. | (all): Retighten flange bolts at leaking joints. One repair per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2022\.01[1234]a | Hot Domestic Piping - Small diameter (branches) | Non-structural | Piping | Domestic | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. | 1/4: D2022.011a - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY 2/4: D2022.012a - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY 3/4: D2022.013a - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY 4/4: D2022.014a - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. | (all): Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | component | 5 | 0 | 0 | 0 | rapid | 0
1 | D2022\.01[34]b | Hot Domestic Piping - Small diameter (bracing), SDC D+ | Non-structural | Piping | Domestic | Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2022.013b - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY 2/2: D2022.014b - Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | (all): Replace failed supports. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2022\.02[1234]a | Hot Domestic Piping - Large diameter (mains) | Non-structural | Piping | Domestic | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | 1/4: D2022.021a - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY 2/4: D2022.022a - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY 3/4: D2022.023a - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY 4/4: D2022.024a - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | (all): Retighten flange bolts at leaking joints. One joint per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2022\.02[1234]a | Hot Domestic Piping - Large diameter (mains) | Non-structural | Piping | Domestic | Pipe Break - 1 break per 1000 feet of pipe. | 1/4: D2022.021a - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY 2/4: D2022.022a - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY 3/4: D2022.023a - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY 4/4: D2022.024a - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Pipe Break - 1 break per 1000 feet of pipe. | (all): Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | component | 5 | 0 | 0 | 0 | rapid | 0
1 | D2022\.02[1234]b | Hot Domestic Piping - Large diameter (bracing) | Non-structural | Piping | Domestic | Lateral Brace Failure - 1 failure per 1000 foot of pipe. | 1/2: D2022.023b - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY 2/2: D2022.024b - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Lateral Brace Failure - 1 failure per 1000 foot of pipe. | (all): Replace failed lateral braces. One repair per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2022\.02[1234]b | Hot Domestic Piping - Large diameter (bracing) | Non-structural | Piping | Domestic | Vertical Brace Failure - 1 failure per 1000 feet of pipe. | 1/2: D2022.023b - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY 2/2: D2022.024b - Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Vertical Brace Failure - 1 failure per 1000 feet of pipe. | (all): Replace failed vertical braces. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2031.0[12][34]b | Sanitary Waste Bracing SDC D+ | Non-structural | Piping | Waste | Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | 1/4: D2031.013b - Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F, BRACING FRAGILITY 2/4: D2031.014b - Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY 3/4: D2031.023b - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, BRACING FRAGILITY 4/4: D2031.024b - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | (all): Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | ~~~ 1-2 ~~~ Replace failed supports. ~~~ 3-4 ~~~ Replace failed supports - 0.5 per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2031\.0[12][12]b | Sanitary Waste Bracing SDC A-C | Non-structural | Piping | Waste | Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | 1/4: D2031.011b - Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC A,B, BRACING FRAGILITY 2/4: D2031.012b - Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC C, BRACING FRAGILITY 3/4: D2031.021b - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY 4/4: D2031.022b - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, BRACING FRAGILITY | (all): Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | ~~~ 1-2 ~~~ Replace failed supports. ~~~ 3-4 ~~~ Replace failed supports - 0.5 per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2031\.0[12][12]b | Sanitary Waste Bracing SDC A-C | Non-structural | Piping | Waste | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). | 1/4: D2031.011b - Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC A,B, BRACING FRAGILITY 2/4: D2031.012b - Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC C, BRACING FRAGILITY 3/4: D2031.021b - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY 4/4: D2031.022b - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, BRACING FRAGILITY | (all): Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). | ~~~ 1-2 ~~~ Replace failed 60 ft pipe sections including supports. One repair per 1000 LF. ~~~ 3-4 ~~~ Replace failed supports and 60 ft pipe per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | D2031\.02[1234]a | Sanitary Waste Piping | Non-structural | Piping | Waste | Joints break - 1 break per 1000 feet of pipe. | 1/4: D2031.021a - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY 2/4: D2031.022a - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, PIPING FRAGILITY 3/4: D2031.023a - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, PIPING FRAGILITY 4/4: D2031.024a - Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), PIPING FRAGILITY | (all): Joints break - 1 break per 1000 feet of pipe. | (all): Replace failed 20 ft pipe sections including supports - one per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | D2051\.0[12][1234]a | Chilled Piping | Non-structural | Piping | Chilled | Small/minor leakage | 1/8: D2051.011a - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY 2/8: D2051.012a - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY 3/8: D2051.013a - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY 4/8: D2051.014a - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY 5/8: D2051.021a - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY 6/8: D2051.022a - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY 7/8: D2051.023a - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY 8/8: D2051.024a - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | ~~~ 1-4 ~~~ Small Leakage at joints - 1 leak per 1000 feet of pipe. ~~~ 5-8 ~~~ Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | (all): Retighten flange bolts at leaking joints. One joint per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2051\.0[12][1234]a | Chilled Piping | Non-structural | Piping | Chilled | Large leak/pipe break | 1/8: D2051.011a - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY 2/8: D2051.012a - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY 3/8: D2051.013a - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY 4/8: D2051.014a - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY 5/8: D2051.021a - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY 6/8: D2051.022a - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY 7/8: D2051.023a - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY 8/8: D2051.024a - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | ~~~ 1-4 ~~~ Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. ~~~ 5-8 ~~~ Pipe Break - 1 break per 1000 feet of pipe. | (all): Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | component | 5 | 0 | 0 | 0 | rapid | 0
0 | D2051\.01[12]b | Chilled Water Piping, Small Diameter (Bracing) SDC A-C | Non-structural | Piping | Chilled | Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2051.011b - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY 2/2: D2051.012b - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | (all): Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | ~~~ 1 ~~~ Replace failed supports. ~~~ 2 ~~~ Replace failed supports - 0.5 per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2051\.01[12]b | Chilled Water Piping, Small Diameter (Bracing) SDC A-C | Non-structural | Piping | Chilled | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2051.011b - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY 2/2: D2051.012b - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | (all): Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). | ~~~ 1 ~~~ Replace failed 60 ft pipe sections including supports. One repair per 1000 LF. ~~~ 2 ~~~ Replace failed supports and 60 ft pipe per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2051\.01[34]b | Chilled Water Piping, Small Diameter (Bracing) SDC D+ | Non-structural | Piping | Chilled | Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2051.013b - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY 2/2: D2051.014b - Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | (all): Replace failed supports - 0.5 per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2051\.02[12]b | Chilled Water Piping, Large Diameter (Bracing) SDC A-C | Non-structural | Piping | Chilled | Vertical Brace Failure - 1 failure per 1000 feet of pipe. | 1/2: D2051.021b - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, BRACING FRAGILITY 2/2: D2051.022b - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, BRACING FRAGILITY | (all): Vertical Brace Failure - 1 failure per 1000 feet of pipe. | (all): Replace failed vertical braces. One repair per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2051\.02[34]b | Chilled Water Piping, Large Diameter (Bracing) SDC D+ | Non-structural | Piping | Chilled | Lateral brace failure | 1/2: D2051.023b - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY 2/2: D2051.024b - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | ~~~ 1 ~~~ Lateral Brace Failure - 0.01 failures per 20 foot pipe section. ~~~ 2 ~~~ Lateral Brace Failure - 1 failure per 1000 foot of pipe. | ~~~ 1 ~~~ Replace failed lateral braces. ~~~ 2 ~~~ Replace failed lateral braces. One repair per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2051\.02[34]b | Chilled Water Piping, Large Diameter (Bracing) SDC D+ | Non-structural | Piping | Chilled | Vertical Brace Failure - 1 failure per 1000 feet of pipe. | 1/2: D2051.023b - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY 2/2: D2051.024b - Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Vertical Brace Failure - 1 failure per 1000 feet of pipe. | (all): Replace failed vertical braces. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2061\.01[12]b | Steam Piping - Small diameter (Bracing) SDC A-C | Non-structural | Piping | Steam | Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2061.011b - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY 2/2: D2061.012b - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | (all): Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | (all): Replace failed supports - 0.5 per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2061\.01[12]b | Steam Piping - Small diameter (Bracing) SDC A-C | Non-structural | Piping | Steam | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2061.011b - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY 2/2: D2061.012b - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | (all): Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). | (all): Replace failed supports and 60 ft pipe per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2061\.01[1234]a | Steam Piping - Small diameter (branches) | Non-structural | Piping | Steam | Small Leakage at joints - 1 leak per 1000 feet of pipe. | 1/4: D2061.011a - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY 2/4: D2061.012a - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY 3/4: D2061.013a - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY 4/4: D2061.014a - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Small Leakage at joints - 1 leak per 1000 feet of pipe. | (all): Retighten flange bolts at leaking joints. One joint per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2061\.01[1234]a | Steam Piping - Small diameter (branches) | Non-structural | Piping | Steam | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. | 1/4: D2061.011a - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY 2/4: D2061.012a - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY 3/4: D2061.013a - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY 4/4: D2061.014a - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. | (all): Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | component | 5 | 0 | 0 | 0 | rapid | 0
0 | D2061\.01[34]b | Steam Piping - Small diameter (Bracing) SDC D+ | Non-structural | Piping | Steam | Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | 1/2: D2061.013b - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY 2/2: D2061.014b - Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Isolated support failure w/o leakage - 0.5 support failures per 1000 feet of pipe (assuming supports every 20 feet). | (all): Replace failed supports - 0.5 per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2061\.02[1234]a | Steam Piping - Large diameter (mains) | Non-structural | Piping | Steam | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | 1/4: D2061.023a - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY 2/4: D2061.024a - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY 3/4: D2061.021a - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY 4/4: D2061.022a - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | (all): Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | (all): Retighten flange bolts at leaking joints. One joint per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D2061\.02[1234]a | Steam Piping - Large diameter (mains) | Non-structural | Piping | Steam | Pipe Break - 1 break per 1000 feet of pipe. | 1/4: D2061.023a - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY 2/4: D2061.024a - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY 3/4: D2061.021a - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY 4/4: D2061.022a - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | (all): Pipe Break - 1 break per 1000 feet of pipe. | (all): Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | component | 5 | 0 | 0 | 0 | rapid | 0
0 | D2061\.02[34]b | Steam Piping - Large diameter (bracing) SDC D+ | Non-structural | Piping | Steam | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | 1/2: D2061.023b - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY 2/2: D2061.024b - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Lateral Brace Failure - 1 failure per 1000 feet of pipe. | (all): Replace failed supports, one per 1000 LF. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D2061\.02[34]b | Steam Piping - Large diameter (bracing) SDC D+ | Non-structural | Piping | Steam | Vertical Brace Failure - 1 failure per 1000 feet of pipe | 1/2: D2061.023b - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY 2/2: D2061.024b - Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | (all): Vertical Brace Failure - 1 failure per 1000 feet of pipe | (all): Replace failed supports, one per 1000 LF. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3031\.01(1[abcd]¦[23][behk]) | Chiller Equipment | Non-structural | HVAC | Chiller | Inoperative equipment | 1/12: D3031.011a - Chiller - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/12: D3031.011b - Chiller - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/12: D3031.011c - Chiller - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/12: D3031.011d - Chiller - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/12: D3031.012b - Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 6/12: D3031.012e - Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 7/12: D3031.012h - Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 8/12: D3031.012k - Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 9/12: D3031.013b - Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 10/12: D3031.013e - Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 11/12: D3031.013h - Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 12/12: D3031.013k - Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Damaged, inoperative. ~~~ 5-12 ~~~ Damaged, inoperative but anchorage is OK. | (all): Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3031\.01[23][adgj] | Chiller Anchorage | Non-structural | HVAC | Chiller | Anchorage failure. | 1/8: D3031.012a - Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/8: D3031.012d - Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 3/8: D3031.012g - Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 4/8: D3031.012j - Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 5/8: D3031.013a - Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 6/8: D3031.013d - Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 7/8: D3031.013g - Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 8/8: D3031.013j - Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3031\.01[23][adgj] | Chiller Anchorage | Non-structural | HVAC | Chiller | Anchorage failure & Equipment damaged beyond repair. | 1/8: D3031.012a - Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/8: D3031.012d - Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 3/8: D3031.012g - Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 4/8: D3031.012j - Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 5/8: D3031.013a - Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 6/8: D3031.013d - Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 7/8: D3031.013g - Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 8/8: D3031.013j - Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3031\.01[23][cfil] | Chiller Equipment Anchorage Combined | Non-structural | HVAC | Chiller | Anchorage failure. | 1/8: D3031.012c - Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3031.012f - Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3031.012i - Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3031.012l - Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3031.013c - Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3031.013f - Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3031.013i - Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3031.013l - Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3031\.01[23][cfil] | Chiller Equipment Anchorage Combined | Non-structural | HVAC | Chiller | Anchorage failure & Equipment damaged beyond repair. | 1/8: D3031.012c - Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3031.012f - Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3031.012i - Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3031.012l - Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3031.013c - Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3031.013f - Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3031.013i - Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3031.013l - Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3031\.01[23][cfil] | Chiller Equipment Anchorage Combined | Non-structural | HVAC | Chiller | Damaged, Inoperative but anchorage is OK. | 1/8: D3031.012c - Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3031.012f - Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3031.012i - Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3031.012l - Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3031.013c - Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3031.013f - Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3031.013i - Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3031.013l - Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged, Inoperative but anchorage is OK. | (all): Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3031\.02(1[abcd]¦[23][behk]) | Cooling Tower Equipment | Non-structural | HVAC | Cooling Tower | Damaged equipment, requires replacement | 1/12: D3031.021a - Cooling Tower - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/12: D3031.021b - Cooling Tower - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/12: D3031.021c - Cooling Tower - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/12: D3031.021d - Cooling Tower - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/12: D3031.022b - Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 6/12: D3031.022e - Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 7/12: D3031.022h - Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 8/12: D3031.022k - Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 9/12: D3031.023b - Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 10/12: D3031.023e - Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 11/12: D3031.023h - Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 12/12: D3031.023k - Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Damaged equipment and attached piping. ~~~ 5-12 ~~~ Damaged equipment and attached piping but anchorage is OK. | (all): Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3031\.02[23][adgj] | Cooling Tower Anchorage | Non-structural | HVAC | Cooling Tower | Anchorage failure. | 1/8: D3031.022a - Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/8: D3031.022d - Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 3/8: D3031.022g - Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 4/8: D3031.022j - Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 5/8: D3031.023a - Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 6/8: D3031.023d - Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 7/8: D3031.023g - Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 8/8: D3031.023j - Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3031\.02[23][adgj] | Cooling Tower Anchorage | Non-structural | HVAC | Cooling Tower | Anchorage failure & Equipment damaged beyond repair. | 1/8: D3031.022a - Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/8: D3031.022d - Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 3/8: D3031.022g - Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 4/8: D3031.022j - Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 5/8: D3031.023a - Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 6/8: D3031.023d - Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 7/8: D3031.023g - Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 8/8: D3031.023j - Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3031\.02[23][cfil] | Cooling Tower Equipment Anchorage Combined | Non-structural | HVAC | Cooling Tower | Anchorage failure. | 1/8: D3031.022c - Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3031.022f - Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3031.022i - Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3031.022l - Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3031.023c - Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3031.023f - Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3031.023i - Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3031.023l - Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3031\.02[23][cfil] | Cooling Tower Equipment Anchorage Combined | Non-structural | HVAC | Cooling Tower | Anchorage failure & Equipment damaged beyond repair. | 1/8: D3031.022c - Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3031.022f - Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3031.022i - Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3031.022l - Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3031.023c - Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3031.023f - Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3031.023i - Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3031.023l - Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3031\.02[23][cfil] | Cooling Tower Equipment Anchorage Combined | Non-structural | HVAC | Cooling Tower | Damaged equipment and attached piping but anchorage OK. | 1/8: D3031.022c - Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3031.022f - Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3031.022i - Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3031.022l - Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3031.023c - Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3031.023f - Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3031.023i - Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3031.023l - Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged equipment and attached piping but anchorage OK. | (all): Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3032\.01(1[abcd]¦[23][behk]) | Compressor Equipment (RTU) | Non-structural | HVAC | Compressor | Equipment does not function, motor damaged (requires repair) | 1/12: D3032.011a - Compressor - Capacity: Small non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/12: D3032.011b - Compressor - Capacity: Large non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/12: D3032.011c - Compressor - Capacity: Small medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/12: D3032.011d - Compressor - Capacity: Large medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/12: D3032.012b - Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 6/12: D3032.012e - Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 7/12: D3032.012h - Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 8/12: D3032.012k - Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 9/12: D3032.013b - Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 10/12: D3032.013e - Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 11/12: D3032.013h - Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 12/12: D3032.013k - Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Equipment does not function. Motor is damaged. ~~~ 5-12 ~~~ Equipment does not function but anchorage is OK. Motor is damaged. | (all): Repair motor. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3032\.01(1[abcd]¦[23][behk]) | Compressor Equipment (RTU) | Non-structural | HVAC | Compressor | Equipment does not function, motor damaged beyond repair | 1/12: D3032.011a - Compressor - Capacity: Small non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/12: D3032.011b - Compressor - Capacity: Large non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/12: D3032.011c - Compressor - Capacity: Small medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/12: D3032.011d - Compressor - Capacity: Large medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/12: D3032.012b - Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 6/12: D3032.012e - Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 7/12: D3032.012h - Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 8/12: D3032.012k - Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 9/12: D3032.013b - Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 10/12: D3032.013e - Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 11/12: D3032.013h - Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 12/12: D3032.013k - Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Equipment does not function. Equipment damaged beyond repair. ~~~ 5-12 ~~~ Equipment does not function but anchorage is OK. Equipment damaged beyond repair. | (all): Replace equipment. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3032\.01[23][adgj] | Compressor Anchorage (RTU) | Non-structural | HVAC | Compressor | Anchorage failure. | 1/8: D3032.012a - Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/8: D3032.012d - Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 3/8: D3032.012g - Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 4/8: D3032.012j - Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 5/8: D3032.013a - Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 6/8: D3032.013d - Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 7/8: D3032.013g - Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 8/8: D3032.013j - Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3032\.01[23][adgj] | Compressor Anchorage (RTU) | Non-structural | HVAC | Compressor | Anchorage failure & Equipment damaged beyond repair. | 1/8: D3032.012a - Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/8: D3032.012d - Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 3/8: D3032.012g - Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 4/8: D3032.012j - Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 5/8: D3032.013a - Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 6/8: D3032.013d - Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 7/8: D3032.013g - Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 8/8: D3032.013j - Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3032\.01[23][cfil] | Compressor Equip and Anchorage Combo | Non-structural | HVAC | Compressor | Anchorage failure. | 1/8: D3032.012c - Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3032.012f - Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3032.012i - Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3032.012l - Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3032.013c - Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3032.013f - Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3032.013i - Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3032.013l - Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3032\.01[23][cfil] | Compressor Equip and Anchorage Combo | Non-structural | HVAC | Compressor | Anchorage failure & Equipment damaged beyond repair. | 1/8: D3032.012c - Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3032.012f - Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3032.012i - Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3032.012l - Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3032.013c - Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3032.013f - Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3032.013i - Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3032.013l - Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3032\.01[23][cfil] | Compressor Equip and Anchorage Combo | Non-structural | HVAC | Compressor | Motor damaged but anchorage is OK. | 1/8: D3032.012c - Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3032.012f - Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3032.012i - Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3032.012l - Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3032.013c - Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3032.013f - Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3032.013i - Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3032.013l - Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Motor damaged but anchorage is OK. | ~~~ 1-4 ~~~ Repair Motor - Anchorage and Concrete do not require replacement ~~~ 5-8 ~~~ Repair Motor - Anchorage and Concrete do not require repair. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3032\.01[23][cfil] | Compressor Equip and Anchorage Combo | Non-structural | HVAC | Compressor | Equipment damaged beyond repair but anchorage is OK. | 1/8: D3032.012c - Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D3032.012f - Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D3032.012i - Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D3032.012l - Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D3032.013c - Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D3032.013f - Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D3032.013i - Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D3032.013l - Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment damaged beyond repair but anchorage is OK. | (all): Replace and install equipment including new anchorage if anchorage is post-installed. | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3041\.0[12]1[abcd] | Air distribution systems: Ducting less than 6 sq ft (branches) | Non-structural | HVAC | Air Dist | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | 1/8: D3041.011a - HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B 2/8: D3041.011b - HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC C 3/8: D3041.011c - HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F 4/8: D3041.011d - HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) 5/8: D3041.021a - HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC A or B 6/8: D3041.021b - HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC C 7/8: D3041.021c - HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F 8/8: D3041.021d - HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | (all): Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | (all): Replace failed supports and repair ducting in vicinity of failed supports. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 1 | 3 | 0 | rapid | 0
0 | D3041\.0[12]1[abcd] | Air distribution systems: Ducting less than 6 sq ft (branches) | Non-structural | HVAC | Air Dist | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. | 1/8: D3041.011a - HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B 2/8: D3041.011b - HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC C 3/8: D3041.011c - HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F 4/8: D3041.011d - HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) 5/8: D3041.021a - HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC A or B 6/8: D3041.021b - HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC C 7/8: D3041.021c - HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F 8/8: D3041.021d - HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | (all): Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. | (all): Replace sections of failed ducting and supports. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0.1 | component | 5 | 1 | 3 | 0 | rapid | 0
1 | D3041\.0[12]2[abcd] | Air distribution systems: Ducting greater than 6 sq ft (mains) | Non-structural | HVAC | Air Dist | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | 1/8: D3041.012a - HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC A or B 2/8: D3041.012b - HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC C 3/8: D3041.012c - HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F 4/8: D3041.012d - HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) 5/8: D3041.022a - HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC A or B 6/8: D3041.022b - HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC C 7/8: D3041.022c - HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F 8/8: D3041.022d - HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | (all): Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | (all): Replace failed supports and repair ducting in vicinity of failed supports. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 1 | 3 | 0 | rapid | 0
1 | D3041\.0[12]2[abcd] | Air distribution systems: Ducting greater than 6 sq ft (mains) | Non-structural | HVAC | Air Dist | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. | 1/8: D3041.012a - HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC A or B 2/8: D3041.012b - HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC C 3/8: D3041.012c - HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F 4/8: D3041.012d - HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) 5/8: D3041.022a - HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC A or B 6/8: D3041.022b - HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC C 7/8: D3041.022c - HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F 8/8: D3041.022d - HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | (all): Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. | (all): Replace sections of failed ducting and supports. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0.1 | component | 5 | 1 | 3 | 0 | rapid | 0
0 | D3041\.001[abcd] | Air distribution systems: HVAC Fan with vibration isolator | Non-structural | HVAC | Air Dist | Bellows fails at fans. | 1/4: D3041.001a - HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC A or B 2/4: D3041.001b - HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC C 3/4: D3041.001c - HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F 4/4: D3041.001d - HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F (OSHPD or sim) | (all): Bellows fails at fans. | (all): Replace failed bellows. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3041\.001[abcd] | Air distribution systems: HVAC Fan with vibration isolator | Non-structural | HVAC | Air Dist | Fan dislodges from isolators and drops. | 1/4: D3041.001a - HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC A or B 2/4: D3041.001b - HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC C 3/4: D3041.001c - HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F 4/4: D3041.001d - HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F (OSHPD or sim) | (all): Fan dislodges from isolators and drops. | (all): Replace fan, isolators and section of ducting to which fan is connected. | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | D3041\.002[abcd] | Air distribution systems: HVAC Fan w/o vibration isolator | Non-structural | HVAC | Air Dist | Bellows fails at fans. | 1/4: D3041.002a - HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC A or B 2/4: D3041.002b - HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC C 3/4: D3041.002c - HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F 4/4: D3041.002d - HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F (OSHPD or sim) | (all): Bellows fails at fans. | (all): Replace failed bellows. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3041\.03\w+ | Air distribution systems: HVAC drops | Non-structural | HVAC | Air Dist | HVAC drops or diffusers dislodges and falls. | 1/6: D3041.031a - HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC A or B 2/6: D3041.031b - HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC C 3/6: D3041.032a - HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC A or B 4/6: D3041.032b - HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC C 5/6: D3041.032c - HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F 6/6: D3041.032d - HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F (OSHPD or sim) | (all): HVAC drops or diffusers dislodges and falls. | (all): Replace diffuser/drop and sections of ceiling and ducting in vicinity to which diffuser/drop is connected. | 1 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 10 | component | 3 | 0 | 0 | 0 | rapid | 0
1 | D3041\.04\w+ | Air distribution systems: Variable Air Volume | Non-structural | HVAC | Air Dist | Coil damages connection to plumbing. Leakage of hot water. | 1/2: D3041.041a - Variable Air Volume (VAV) box with in-line coil, SDC A or B 2/2: D3041.041b - Variable Air Volume (VAV) box with in-line coil, SDC C | (all): Coil damages connection to plumbing. Leakage of hot water. | (all): Replace coil and cleanup water damage. | 1 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 10 | component | 3 | 0 | 0 | 0 | rapid | 0
0 | D3041\.10(1a¦[23]b) | HVAC Fan Equipment (exhaust) | Non-structural | HVAC | Air Dist | Inoperative equipment | 1/3: D3041.101a - HVAC Fan - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/3: D3041.102b - HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 3/3: D3041.103b - HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1 ~~~ Damaged, inoperative. ~~~ 2-3 ~~~ Damaged, inoperative but anchorage is OK. | ~~~ 1-2 ~~~ Replace equipment. ~~~ 3 ~~~ Repair equipment. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3041\.10[23]a | HVAC Fan Anchorage (exhaust) | Non-structural | HVAC | Air Dist | Anchorage failure. | 1/2: D3041.102a - HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/2: D3041.103a - HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3041\.10[23]a | HVAC Fan Anchorage (exhaust) | Non-structural | HVAC | Air Dist | Anchorage failure & Equipment damaged beyond repair. | 1/2: D3041.102a - HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/2: D3041.103a - HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Repair anchorage and replace equipment. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | D3041\.10[23]c | HVAC Fan Equipment Anchorage Combined (exhaust) | Non-structural | HVAC | Air Dist | Anchorage failure. | 1/2: D3041.102c - HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/2: D3041.103c - HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3041\.10[23]c | HVAC Fan Equipment Anchorage Combined (exhaust) | Non-structural | HVAC | Air Dist | Anchorage failure & Equipment damaged beyond repair. | 1/2: D3041.102c - HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/2: D3041.103c - HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Repair anchorage and replace equipment. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3041\.10[23]c | HVAC Fan Equipment Anchorage Combined (exhaust) | Non-structural | HVAC | Air Dist | Damaged, Inoperative but anchorage is OK | 1/2: D3041.102c - HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/2: D3041.103c - HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged, Inoperative but anchorage is OK | (all): Repair equipment. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
1 | D3052\.01(1[abcd]¦3[behk]) | Air handeling Equipment | Non-structural | HVAC | AHU | Equipment damaged - repair | 1/8: D3052.011a - Air Handling Unit - Capacity: <5000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/8: D3052.011b - Air Handling Unit - Capacity: 5000 to <10000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/8: D3052.011c - Air Handling Unit - Capacity: 10000 to <25000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/8: D3052.011d - Air Handling Unit - Capacity: 25000 to <40000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/8: D3052.013b - Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 6/8: D3052.013e - Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 7/8: D3052.013h - Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 8/8: D3052.013k - Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Equipment does not function. Damage to attached ducting or piping. ~~~ 5-8 ~~~ Equipment does not function but anchorage is OK. Damage to attached ducting or piping. | (all): Repair attached ducting or piping. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3052\.01(1[abcd]¦3[behk]) | Air handeling Equipment | Non-structural | HVAC | AHU | Equipment damaged - replace | 1/8: D3052.011a - Air Handling Unit - Capacity: <5000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/8: D3052.011b - Air Handling Unit - Capacity: 5000 to <10000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/8: D3052.011c - Air Handling Unit - Capacity: 10000 to <25000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/8: D3052.011d - Air Handling Unit - Capacity: 25000 to <40000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/8: D3052.013b - Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 6/8: D3052.013e - Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 7/8: D3052.013h - Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 8/8: D3052.013k - Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Equipment does not function Equipment damaged beyond repair. ~~~ 5-8 ~~~ Equipment does not function but anchorage is OK. Equipment damaged beyond repair. | (all): Replace equipment. Remove, repair offsite, and reinstall air handler. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3052\.013[adgj] | Air handeling Anchorage | Non-structural | HVAC | AHU | Anchorage failure. | 1/4: D3052.013a - Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 2/4: D3052.013d - Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 3/4: D3052.013g - Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 4/4: D3052.013j - Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3052\.013[adgj] | Air handeling Anchorage | Non-structural | HVAC | AHU | Anchorage failure & Equipment damaged beyond repair. | 1/4: D3052.013a - Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 2/4: D3052.013d - Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 3/4: D3052.013g - Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 4/4: D3052.013j - Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3052\.013[cfil] | Air Handling Equipment and Anchorage | Non-structural | HVAC | AHU | Anchorage failure. | 1/4: D3052.013c - Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D3052.013f - Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D3052.013i - Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D3052.013l - Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3052\.013[cfil] | Air Handling Equipment and Anchorage | Non-structural | HVAC | AHU | Anchorage failure & Equipment damaged beyond repair. | 1/4: D3052.013c - Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D3052.013f - Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D3052.013i - Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D3052.013l - Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3052\.013[cfil] | Air Handling Equipment and Anchorage | Non-structural | HVAC | AHU | Damage to attached ducting or piping but anchorage is OK. | 1/4: D3052.013c - Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D3052.013f - Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D3052.013i - Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D3052.013l - Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damage to attached ducting or piping but anchorage is OK. | (all): Repair attached ducting or piping - equipment does not require replacement and anchorage does not require repair | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3052\.013[cfil] | Air Handling Equipment and Anchorage | Non-structural | HVAC | AHU | Equipment damaged beyond repair but anchorage is OK. | 1/4: D3052.013c - Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D3052.013f - Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D3052.013i - Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D3052.013l - Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment damaged beyond repair but anchorage is OK. | (all): Replace and install equipment including new anchorage if anchorage is post-installed. | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3067\.01(1a¦2b) | HVAC Control Panel Equipment | Non-structural | HVAC | Control Panel | Equipment damaged - replace parts of equipment (relays, circuit boards) | 1/2: D3067.011a - Control Panel - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/2: D3067.012b - Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1 ~~~ Damaged, inoperative. ~~~ 2 ~~~ Damaged, inoperative but anchorage is OK. | (all): Replace some components (relays, circuit boards). | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3067\.012a | HVAC Control Panel Anchorage | Non-structural | HVAC | Control Panel | Anchorage failure. | 1/1: D3067.012a - Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D3067\.012a | HVAC Control Panel Anchorage | Non-structural | HVAC | Control Panel | Anchorage failure & Equipment damaged beyond repair. | 1/1: D3067.012a - Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3067\.012c | HVAC Control Panel Equipment Anchorage Combined | Non-structural | HVAC | Control Panel | Anchorage failure. | 1/1: D3067.012c - Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3067\.012c | HVAC Control Panel Equipment Anchorage Combined | Non-structural | HVAC | Control Panel | Anchorage failure & Equipment damaged beyond repair. | 1/1: D3067.012c - Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D3067\.012c | HVAC Control Panel Equipment Anchorage Combined | Non-structural | HVAC | Control Panel | Damaged, Inoperative but anchorage is OK | 1/1: D3067.012c - Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged, Inoperative but anchorage is OK | (all): Replace some components (relays, circuit boards | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D4011\.0(3[12]a¦[4567]\w+) | Fire Sprinkler Water Supply: Fire sprinkler drop 2 DS | Non-structural | Piping | Fire | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | 1/12: D4011.031a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B 2/12: D4011.032a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC C 3/12: D4011.041a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC A or B 4/12: D4011.042a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC C 5/12: D4011.053a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F 6/12: D4011.054a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) 7/12: D4011.063a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F 8/12: D4011.064a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) 9/12: D4011.071a - Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC A or B 10/12: D4011.072a - Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC C 11/12: D4011.073a - Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F 12/12: D4011.074a - Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | (all): Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | (all): Replace sprinkler drops and minor water cleanup at broken joints. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D4011\.0(3[12]a¦[4567]\w+) | Fire Sprinkler Water Supply: Fire sprinkler drop 2 DS | Non-structural | Piping | Fire | Drop Joints Break - Major Leakage - 0.01 breaks per drop. | 1/12: D4011.031a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B 2/12: D4011.032a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC C 3/12: D4011.041a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC A or B 4/12: D4011.042a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC C 5/12: D4011.053a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F 6/12: D4011.054a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) 7/12: D4011.063a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F 8/12: D4011.064a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) 9/12: D4011.071a - Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC A or B 10/12: D4011.072a - Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC C 11/12: D4011.073a - Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F 12/12: D4011.074a - Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | (all): Drop Joints Break - Major Leakage - 0.01 breaks per drop. | (all): Replace sprinkler drops and major water cleanup at broken joints | 2 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | D4011\.02\w+ | Fire Sprinkler Water Supply: Piping and Pipe Bracing | Non-structural | Piping | Fire | Spraying & Dripping Leakage at joints - 0.02 leaks per 20 ft section of pipe. | 1/4: D4011.021a - Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY 2/4: D4011.022a - Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC C, PIPING FRAGILITY 3/4: D4011.023a - Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - Poorly designed bracing, SDC D, E, or F , PIPING FRAGILITY 4/4: D4011.024a - Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - with designed bracing, SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Spraying & Dripping Leakage at joints - 0.02 leaks per 20 ft section of pipe. | (all): Replace leaking joints and minor water cleanup. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D4011\.02\w+ | Fire Sprinkler Water Supply: Piping and Pipe Bracing | Non-structural | Piping | Fire | Joints Break - Major Leakage - 0.02 breaks per 20 ft section of pipe. | 1/4: D4011.021a - Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY 2/4: D4011.022a - Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC C, PIPING FRAGILITY 3/4: D4011.023a - Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - Poorly designed bracing, SDC D, E, or F , PIPING FRAGILITY 4/4: D4011.024a - Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - with designed bracing, SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | (all): Joints Break - Major Leakage - 0.02 breaks per 20 ft section of pipe. | (all): Replace 20 ft section of pipe, joints and major water cleanup at leaking joints. | 2 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | component | 5 | 0 | 0 | 0 | rapid | 0
1 | D4011\.03[34]a | Fire Sprinkler Drop | Non-structural | Piping | Fire | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | 1/2: D4011.033a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F 2/2: D4011.034a - Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | (all): Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | (all): Replace sprinkler drops and minor water cleanup at broken joints. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 5 | 0 | 0 | 0 | rapid | 0
0 | D5011\.01(1[abcd]¦3[behk]) | Transformer Equipment | Non-structural | Electrical | Transformer | Damaged - Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. | 1/8: D5011.011a - Transformer/primary service - Capacity: <100 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/8: D5011.011b - Transformer/primary service - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/8: D5011.011c - Transformer/primary service - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/8: D5011.011d - Transformer/primary service - Capacity: 750 to 1500 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/8: D5011.013b - Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 6/8: D5011.013e - Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 7/8: D5011.013h - Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 8/8: D5011.013k - Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Damaged, inoperative. ~~~ 5-8 ~~~ Damaged, inoperative but anchorage is OK. | (all): Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5011\.013[adgj] | Transformer Anchorage | Non-structural | Electrical | Transformer | Anchorage failure. | 1/4: D5011.013a - Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 2/4: D5011.013d - Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 3/4: D5011.013g - Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 4/4: D5011.013j - Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5011\.013[adgj] | Transformer Anchorage | Non-structural | Electrical | Transformer | Anchorage failure & Equipment damaged beyond repair. | 1/4: D5011.013a - Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 2/4: D5011.013d - Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 3/4: D5011.013g - Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 4/4: D5011.013j - Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5011\.013[cfil] | Transformer Equipment Anchorage Combined | Non-structural | Electrical | Transformer | Anchorage failure. | 1/4: D5011.013c - Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5011.013f - Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5011.013i - Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5011.013l - Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5011\.013[cfil] | Transformer Equipment Anchorage Combined | Non-structural | Electrical | Transformer | Anchorage failure & Equipment damaged beyond repair. | 1/4: D5011.013c - Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5011.013f - Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5011.013i - Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5011.013l - Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5011\.013[cfil] | Transformer Equipment Anchorage Combined | Non-structural | Electrical | Transformer | Damaged, Inoperative but anchorage is OK. | 1/4: D5011.013c - Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5011.013f - Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5011.013i - Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5011.013l - Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged, Inoperative but anchorage is OK. | (all): Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.013[ac] | Motor Control Center Equipment | Non-structural | Electrical | MCC | damaged - replace | 1/2: D5012.013a - Motor Control Center - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/2: D5012.013c - Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1 ~~~ Damaged, inoperative ~~~ 2 ~~~ Damaged, inoperative but anchorage is OK. | (all): Replace equipment. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5012\.013b | Motor Control Center Anchorage | Non-structural | Electrical | MCC | Anchorage failure. | 1/1: D5012.013b - Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5012\.013b | Motor Control Center Anchorage | Non-structural | Electrical | MCC | Anchorage failure & Equipment damaged beyond repair. | 1/1: D5012.013b - Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.013d | Motor Control Center Equipment Anchorage Combined | Non-structural | Electrical | MCC | Anchorage failure. | 1/1: D5012.013d - Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): If anchored repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.013d | Motor Control Center Equipment Anchorage Combined | Non-structural | Electrical | MCC | Anchorage failure & Equipment damaged beyond repair. | 1/1: D5012.013d - Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad if anchored. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.013d | Motor Control Center Equipment Anchorage Combined | Non-structural | Electrical | MCC | Damaged, Inoperative but anchorage is OK. | 1/1: D5012.013d - Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged, Inoperative but anchorage is OK. | (all): Replace equipment. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5012\.02(1[abcd]¦3[behk]) | Switchgear Equipment | Non-structural | Electrical | Switchgear | Damaged, replace parts of equipment | 1/8: D5012.021a - Low Voltage Switchgear - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/8: D5012.021b - Low Voltage Switchgear - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/8: D5012.021c - Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/8: D5012.021d - Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/8: D5012.023b - Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 6/8: D5012.023e - Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 7/8: D5012.023h - Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 8/8: D5012.023k - Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Damaged, inoperative. ~~~ 5-8 ~~~ Damaged, inoperative but anchorage is OK. | ~~~ 1-4 ~~~ Replace insulator. ~~~ 5-8 ~~~ Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.023[adgj] | Switchgear Anchorage | Non-structural | Electrical | Switchgear | Anchorage failure. | 1/4: D5012.023a - Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 2/4: D5012.023d - Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 3/4: D5012.023g - Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 4/4: D5012.023j - Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.023[adgj] | Switchgear Anchorage | Non-structural | Electrical | Switchgear | Anchorage failure & Equipment damaged beyond repair. | 1/4: D5012.023a - Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 2/4: D5012.023d - Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 3/4: D5012.023g - Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 4/4: D5012.023j - Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5012\.023[cfil] | Switchgear Equipment Anchorage Combined | Non-structural | Electrical | Switchgear | Anchorage failure. | 1/4: D5012.023c - Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5012.023f - Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5012.023i - Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5012.023l - Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5012\.023[cfil] | Switchgear Equipment Anchorage Combined | Non-structural | Electrical | Switchgear | Anchorage failure & Equipment damaged beyond repair. | 1/4: D5012.023c - Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5012.023f - Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5012.023i - Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5012.023l - Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5012\.023[cfil] | Switchgear Equipment Anchorage Combined | Non-structural | Electrical | Switchgear | Damaged, Inoperative but anchorage is OK. | 1/4: D5012.023c - Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5012.023f - Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5012.023i - Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5012.023l - Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged, Inoperative but anchorage is OK. | (all): Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.03(1[abcd]¦3[behk]) | Distribution Panel Equipment | Non-structural | Electrical | Distribution | Damaged, inoperative but anchorage is OK. | 1/8: D5012.031a - Distribution Panel - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/8: D5012.031b - Distribution Panel - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/8: D5012.031c - Distribution Panel - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/8: D5012.031d - Distribution Panel - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/8: D5012.033b - Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 6/8: D5012.033e - Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 7/8: D5012.033h - Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 8/8: D5012.033k - Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | (all): Damaged, inoperative but anchorage is OK. | (all): Replace equipment | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5012\.033[adgj] | Distribution Panel Anchorage | Non-structural | Electrical | Distribution | Anchorage failure. | 1/4: D5012.033a - Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 2/4: D5012.033d - Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 3/4: D5012.033g - Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 4/4: D5012.033j - Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5012\.033[adgj] | Distribution Panel Anchorage | Non-structural | Electrical | Distribution | Anchorage failure & Equipment damaged beyond repair. | 1/4: D5012.033a - Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 2/4: D5012.033d - Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 3/4: D5012.033g - Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 4/4: D5012.033j - Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.033[cfil] | Distribution Panel Equipment Anchorage Combined | Non-structural | Electrical | Distribution | Anchorage failure. | 1/4: D5012.033c - Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5012.033f - Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5012.033i - Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5012.033l - Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.033[cfil] | Distribution Panel Equipment Anchorage Combined | Non-structural | Electrical | Distribution | Anchorage failure & Equipment damaged beyond repair. | 1/4: D5012.033c - Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5012.033f - Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5012.033i - Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5012.033l - Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5012\.033[cfil] | Distribution Panel Equipment Anchorage Combined | Non-structural | Electrical | Distribution | Damaged, Inoperative but anchorage is OK. | 1/4: D5012.033c - Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 2/4: D5012.033f - Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 3/4: D5012.033i - Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 4/4: D5012.033l - Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged, Inoperative but anchorage is OK. | (all): Replace equipment. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.01(1a¦3b) | Battery Rack Equipment | Non-structural | Electrical | Battery | Batteries fall, crack cases, dislodge conductors, or are otherwise damaged | 1/2: D5092.011a - Battery Rack - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/2: D5092.013b - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1 ~~~ Damaged, inoperative. Batteries fall, crack cases, dislodge conductors, or are otherwise damaged. ~~~ 2 ~~~ Damaged, inoperative but anchorage is OK. Batteries fall, crack cases, dislodge conductors, or are otherwise damaged. | (all): Replace batteries. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.01(1a¦3b) | Battery Rack Equipment | Non-structural | Electrical | Battery | Batteries spill battery acid. | 1/2: D5092.011a - Battery Rack - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/2: D5092.013b - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | (all): Batteries spill battery acid. | (all): Clean up spilled acid. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.01(1a¦3b) | Battery Rack Equipment | Non-structural | Electrical | Battery | Battery rack collapses. | 1/2: D5092.011a - Battery Rack - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/2: D5092.013b - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | (all): Battery rack collapses. | (all): Replace battery rack. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.013a | Battery Rack Anchorage | Non-structural | Electrical | Battery | Anchorage failure. | 1/1: D5092.013a - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.013a | Battery Rack Anchorage | Non-structural | Electrical | Battery | Anchorage failure & Equipment damaged beyond repair. | 1/1: D5092.013a - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.013c | Battery Rack Equipment Anchorage Combined | Non-structural | Electrical | Battery | Anchorage failure. | 1/1: D5092.013c - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.013c | Battery Rack Equipment Anchorage Combined | Non-structural | Electrical | Battery | Anchorage failure & Equipment damaged beyond repair. | 1/1: D5092.013c - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.013c | Battery Rack Equipment Anchorage Combined | Non-structural | Electrical | Battery | Equipment is damaged and inoperative. | 1/1: D5092.013c - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment is damaged and inoperative. | (all): Replace batteries. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.013c | Battery Rack Equipment Anchorage Combined | Non-structural | Electrical | Battery | Equipment is damaged and inoperative. | 1/1: D5092.013c - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment is damaged and inoperative. | (all): Replace batteries and clean up acid. | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.013c | Battery Rack Equipment Anchorage Combined | Non-structural | Electrical | Battery | Equipment is damaged and inoperative. | 1/1: D5092.013c - Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment is damaged and inoperative. | (all): Replace rack including batteries and clean up acid. | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.02(1a¦3b) | Battery Charger Equipment | Non-structural | Electrical | Battery | Damaged, inoperative but anchorage is OK. | 1/2: D5092.021a - Battery Charger - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/2: D5092.023b - Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | (all): Damaged, inoperative but anchorage is OK. | (all): Service for intermittent voltage output or for blown surge suppressor. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.02(1a¦3b) | Battery Charger Equipment | Non-structural | Electrical | Battery | Damaged, inoperative but anchorage is OK. Equipment damaged beyond repair. | 1/2: D5092.021a - Battery Charger - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/2: D5092.023b - Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | (all): Damaged, inoperative but anchorage is OK. Equipment damaged beyond repair. | (all): Replace equipment. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.023a | Battery Charger Anchorage | Non-structural | Electrical | Battery | Anchorage failure. | 1/1: D5092.023a - Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.023a | Battery Charger Anchorage | Non-structural | Electrical | Battery | Anchorage failure & Equipment damaged beyond repair. | 1/1: D5092.023a - Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad / wall. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.023c | Battery Charger Equipment Anchorage Combined | Non-structural | Electrical | Battery | Anchorage failure. | 1/1: D5092.023c - Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.023c | Battery Charger Equipment Anchorage Combined | Non-structural | Electrical | Battery | Anchorage failure & Equipment damaged beyond repair. | 1/1: D5092.023c - Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad / wall. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.023c | Battery Charger Equipment Anchorage Combined | Non-structural | Electrical | Battery | Equipment is damaged and inoperative. | 1/1: D5092.023c - Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment is damaged and inoperative. | (all): Service for intermittent voltage output or for blown surge suppressor. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.023c | Battery Charger Equipment Anchorage Combined | Non-structural | Electrical | Battery | Equipment is damaged and inoperative. | 1/1: D5092.023c - Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment is damaged and inoperative. | (all): Replace equipment. | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03(1[abcd]¦[23][behk]) | Diesel Generator Equipment | Non-structural | Electrical | Generator | Pipes and nozzles damaged | 1/12: D5092.031a - Diesel generator - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/12: D5092.031b - Diesel generator - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/12: D5092.031c - Diesel generator - Capacity: 750 to 1200 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/12: D5092.031d - Diesel generator - Capacity: 1200 to 2000 kVa - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/12: D5092.032b - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 6/12: D5092.032e - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 7/12: D5092.032h - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 8/12: D5092.032k - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 9/12: D5092.033b - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 10/12: D5092.033e - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 11/12: D5092.033h - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 12/12: D5092.033k - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Damaged, inoperative. Pipes and nozzles damaged. ~~~ 5-12 ~~~ Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | (all): Repair fracture pipes and damaged nozzles. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03(1[abcd]¦[23][behk]) | Diesel Generator Equipment | Non-structural | Electrical | Generator | Drive shaft misalignment | 1/12: D5092.031a - Diesel generator - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/12: D5092.031b - Diesel generator - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/12: D5092.031c - Diesel generator - Capacity: 750 to 1200 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/12: D5092.031d - Diesel generator - Capacity: 1200 to 2000 kVa - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/12: D5092.032b - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 6/12: D5092.032e - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 7/12: D5092.032h - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 8/12: D5092.032k - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 9/12: D5092.033b - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 10/12: D5092.033e - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 11/12: D5092.033h - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 12/12: D5092.033k - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Damaged, inoperative. Drive shaft misalignment. ~~~ 5-12 ~~~ Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | (all): Overhaul because of drive shaft misalignment. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03(1[abcd]¦[23][behk]) | Diesel Generator Equipment | Non-structural | Electrical | Generator | Minor electrical damage, e.g., failed relay | 1/12: D5092.031a - Diesel generator - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/12: D5092.031b - Diesel generator - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/12: D5092.031c - Diesel generator - Capacity: 750 to 1200 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/12: D5092.031d - Diesel generator - Capacity: 1200 to 2000 kVa - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/12: D5092.032b - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 6/12: D5092.032e - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 7/12: D5092.032h - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 8/12: D5092.032k - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 9/12: D5092.033b - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 10/12: D5092.033e - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 11/12: D5092.033h - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 12/12: D5092.033k - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Damaged, inoperative. Minor electrical damage, e.g., failed relay. ~~~ 5-12 ~~~ Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | (all): Minor electrical repair e.g., replace relay. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03(1[abcd]¦[23][behk]) | Diesel Generator Equipment | Non-structural | Electrical | Generator | Exhaust line disconnected at expansion bellows | 1/12: D5092.031a - Diesel generator - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 2/12: D5092.031b - Diesel generator - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 3/12: D5092.031c - Diesel generator - Capacity: 750 to 1200 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only 4/12: D5092.031d - Diesel generator - Capacity: 1200 to 2000 kVa - Unanchored equipment that is not vibration isolated - Equipment fragility only 5/12: D5092.032b - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 6/12: D5092.032e - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 7/12: D5092.032h - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 8/12: D5092.032k - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only 9/12: D5092.033b - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 10/12: D5092.033e - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 11/12: D5092.033h - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only 12/12: D5092.033k - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | ~~~ 1-4 ~~~ Damaged, inoperative. Exhaust line disconnected at expansion bellows. ~~~ 5-12 ~~~ Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. | (all): Reconnect exhaust line. | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.03[23][adgj] | Diesel Generator Anchorage | Non-structural | Electrical | Generator | Anchorage failure. | 1/8: D5092.032a - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/8: D5092.032d - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 3/8: D5092.032g - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 4/8: D5092.032j - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 5/8: D5092.033a - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 6/8: D5092.033d - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 7/8: D5092.033g - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 8/8: D5092.033j - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | D5092\.03[23][adgj] | Diesel Generator Anchorage | Non-structural | Electrical | Generator | Anchorage failure & Equipment damaged beyond repair. | 1/8: D5092.032a - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 2/8: D5092.032d - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 3/8: D5092.032g - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 4/8: D5092.032j - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only 5/8: D5092.033a - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 6/8: D5092.033d - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 7/8: D5092.033g - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only 8/8: D5092.033j - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03[23][cfil] | Diesel Generator Equipment Anchorage Combined | Non-structural | Electrical | Generator | Anchorage failure. | 1/8: D5092.032c - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D5092.032f - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D5092.032i - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D5092.032l - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D5092.033c - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D5092.033f - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D5092.033i - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D5092.033l - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure. | (all): Repair anchorage and concrete pad and remount equipment. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03[23][cfil] | Diesel Generator Equipment Anchorage Combined | Non-structural | Electrical | Generator | Anchorage failure & Equipment damaged beyond repair. | 1/8: D5092.032c - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D5092.032f - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D5092.032i - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D5092.032l - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D5092.033c - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D5092.033f - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D5092.033i - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D5092.033l - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Anchorage failure & Equipment damaged beyond repair. | (all): Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03[23][cfil] | Diesel Generator Equipment Anchorage Combined | Non-structural | Electrical | Generator | Damaged, Inoperative but anchorage is OK | 1/8: D5092.032c - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D5092.032f - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D5092.032i - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D5092.032l - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D5092.033c - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D5092.033f - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D5092.033i - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D5092.033l - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Damaged, Inoperative but anchorage is OK | (all): Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03[23][cfil] | Diesel Generator Equipment Anchorage Combined | Non-structural | Electrical | Generator | Equipment is damaged and inoperative but anchorage is OK. | 1/8: D5092.032c - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D5092.032f - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D5092.032i - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D5092.032l - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D5092.033c - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D5092.033f - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D5092.033i - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D5092.033l - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment is damaged and inoperative but anchorage is OK. | (all): Overhaul because of drive shaft misalignment. | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
0 | D5092\.03[23][cfil] | Diesel Generator Equipment Anchorage Combined | Non-structural | Electrical | Generator | Equipment is damaged and inoperative but anchorage is OK. | 1/8: D5092.032c - Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 2/8: D5092.032f - Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 3/8: D5092.032i - Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 4/8: D5092.032l - Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility 5/8: D5092.033c - Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 6/8: D5092.033f - Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 7/8: D5092.033i - Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility 8/8: D5092.033l - Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | (all): Equipment is damaged and inoperative but anchorage is OK. | (all): minor electrical repair e.g., replace relays. | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | NA | 3 | 0 | 0 | 0 | rapid | 0
1 | F1012\.001 | Storage Racks | Non-structural | Contents | Racks | Significant merchandise shedding from rack shelves. | 1/1: F1012.001 - Storage racks designed and installed before 2007, big box retail (12' to 15' tall) | (all): Significant merchandise shedding from rack shelves. | (all): Minor repair to storage rack. Resort and restock shelves. Clean up debris. | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | component | 3 | 1 | 3 | 0 | rapid | 0
1 | F1012\.001 | Storage Racks | Non-structural | Contents | Racks | Significant structural damage to rack structure. | 1/1: F1012.001 - Storage racks designed and installed before 2007, big box retail (12' to 15' tall) | (all): Significant structural damage to rack structure. | (all): Remove and replace storage rack system. Make minor repair to adjacent finishes. Resort and restock shelves. Clean up debris. | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | component | 3 | 1 | 7 | 0 | rapid | 0
0 | E2022\.0[0-2][0-3] | General tenant content on shelves and desks | Non-structural | Contents | General | Spilled and scattered contents | 1/9: E2022.001 - Modular office work stations. 2/9: E2022.010 - Unsecured fragile objects on shelves, unknown restraint 3/9: E2022.011 - Fragile contents secured by museum putty, Velcro or other weak but sticky stuff 4/9: E2022.012 - Fragile contents on shelves in storage cabinets with latches 5/9: E2022.013 - Unsecured fragile objects on shelves, low friction surface 6/9: E2022.020 - Home entertainment equipment, unknown installation 7/9: E2022.021 - Electronic equipment on wall mount brackets 8/9: E2022.022 - Desktop electronics including computers, monitors, stereos, etc on a slip resistant surface 9/9: E2022.023 - Desktop electronics including computers, monitors, stereos, etc, smooth surface | ~~~ 1 ~~~ Wall units need to be adjusted and straightened. Some elements are bent / damaged and need to be replaced. ~~~ 2-5 ~~~ Object falls off shelf or shelf overturns and object breaks or object breaks within cabinet. ~~~ 6-9 ~~~ Falls, does not function. | ~~~ 1 ~~~ Adjust and or straightened wall units. Replace damaged units. Assume a repair cost of 5% of the replacement value. ~~~ 2-5 ~~~ Replace object. Note: user must supply cost of replacement. ~~~ 6-9 ~~~ Replace equipment. User must supply replacement cost. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | component | 3 | 1 | 3 | 0 | rapid | 0
1 | E2022\.10[2-6][ab] | Bookcase | Non-structural | Contents | General | Book case falls over and contents are scattered. Likely damage to bookcase. | 1/10: E2022.102a - Bookcase, 2 shelves, unanchored laterally 2/10: E2022.102b - Bookcase, 2 shelves, anchored laterally 3/10: E2022.103a - Bookcase, 3 shelves, unanchored laterally 4/10: E2022.103b - Bookcase, 3 shelves, anchored laterally 5/10: E2022.104a - Bookcase, 4 shelves, unanchored laterally 6/10: E2022.104b - Bookcase, 4 shelves, anchored laterally 7/10: E2022.105a - Bookcase, 5 shelves, unanchored laterally 8/10: E2022.105b - Bookcase, 5 shelves, anchored laterally 9/10: E2022.106a - Bookcase, 6 shelves, unanchored laterally 10/10: E2022.106b - Bookcase, 6 shelves, anchored laterally | (all): Book case falls over and contents are scattered. Likely damage to bookcase. | (all): Replace bookcase and restack / replace contents. | 1 | NA | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 50 | component | 3 | 1 | 3 | 0 | rapid | 0
0 | E2022\.1[12][245][ab] | Filing Cabinent | Non-structural | Contents | General | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. | 1/8: E2022.112a - Vertical Filing Cabinet, 2 drawer, unanchored laterally 2/8: E2022.112b - Vertical Filing Cabinet, 2 drawer, anchored laterally 3/8: E2022.114a - Vertical Filing Cabinet, 4 drawer, unanchored laterally 4/8: E2022.114b - Vertical Filing Cabinet, 4 drawer, anchored laterally 5/8: E2022.124a - Lateral Filing Cabinet, 2 drawer, unanchored laterally 6/8: E2022.124b - Lateral Filing Cabinet, 2 drawer, anchored laterally 7/8: E2022.125a - Lateral Filing Cabinet, 4 drawer, unanchored laterally 8/8: E2022.125b - Lateral Filing Cabinet, 4 drawer, anchored laterally | (all): Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. | (all): Replace filing cabinet and refile / replace contents. | 1 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | component | 3 | 1 | 3 | 0 | rapid | 0

## Misc
Safety Class
Column Buckling | 3